## Versions
Version | Date | Author | Description | Evolution
0.1 | 2019-03-06 | Pierre, Vadim | Draft
0.2 | 2019-03-08 | Michel, Pierre, Vadim | Reviewed
0.3 | 2019-03-12 | Pierre | Reviewed | Circuit Breakers : Asset type & Current rating (In) IEM3xxx: list & prioization completed Asset type of IEM, PM, Gateway
0.4 | 2019-03-13 | Pierre | Reviewed | All the devices are completed (1st columns A to H) Except: PM8xx, PowerTag 125-160A / PowerTag Rope 2000A / PowerTag C 2DI / PowerTag C iO / Fire Tag / Acti9 OF24 / Acti9 SD24 New Asset columns: Asset SN / Asset Reference / Startup Date
0.5 | 2019-03-22 | Pierre | Reviewed | New ED Asset specific data columns: Breaker Capacity-Curve Type / Pole Number / Rated Voltage / Rated Frequency / Standard / Breaker Category / Incomer / Phase Sequence / Installation UP-DOWN / Pre-Alarm Ir New column: Asset type list ED Asset specific data moved close to ED Asset data MCCB&ACB Circuit Breakers: Relationship between Asset Type & Current Rating added 'NA' fields added for the Asset data
0.6 | 2019-03-27 | Pierre | Reviewed | Columns relative to 'Communicating device' move to the left, before ED Asset, for a better readibility. PM8XX lines fulfiled Product range & Product Model added for : PowerTag C 2DI / PowerTag C iO / TH110 / CL110 / E Sensor TRH&CO2 /EwSenseTemp / OF24 /SD24 For the other lines (except PowerTag 125-160A / PowerTag Rope 2000A), the following columns are fulfiled: Communicating device / Product Range Communicating device / Product model Communicating device / Adress (Modbus ID) ED Asset / Asset type Ed Asset / Asset type List Ed Asset / Current rating (In) Ed Asset / Current rating List (In) Ed Asset / Commodity Ed Asset / Commodity List Ed Asset specific data / Breaker capacity or curve type Ed Asset specific data / Pole Number Ed Asset specific data / Rated voltage Ed Asset specific data / Rated frequency Ed Asset specific data / Frequency Ed Asset specific data / Breaker category Ed Asset specific data / Incomer (flag) Ed Asset specific data / Phase sequence Ed Asset specific data / Installation UP-DOWN Ed Asset specific data / Pre-Alarm Ir (%)
0.7 |  | Pierre | Reviewed | Product range & Product Model added for : "New high rating current" PowerTags
0.8 |  | Pierre | Reviewed | Product range & Product Model & Associated Asset added for : PowerTags Rope, PowerTags 'Square D', New High Rating PowerTags Adjustments after a sharing with Cedric Gauthier (PDM leader)
0.9 |  | Pierre | Reviewed | Asset associations for the new PowerTag160
1.0 |  | Pierre | Reviewed | Prioritization update
1.1 |  | Pierre | Reviewed | New PowerTag (A9 M63 3P+W, A9F63 1P+N 110V, A9F63 3P, A9F63 3P+N 110/230V)
1.2 |  | Pierre | Reviewed | Priorization of the new PowerTag UL (Square D) Priorization of the new PowerTag IEC / VLN110V-VLL230V >> THE PRIORIZATION IS NOW COMPLETED FOR ALL THE DEVICES Switch disconnector (Compact NSX, PowerPact HJL) added NA for Monitored Area (Gateways) TI24 Standard IO: Out Of Scope
1.3 |  | Pierre | Reviewed | Installation UP/DOWN' data: list of the devices with 'NA' is refined Completion of the columns: 'ED Asset (aca Equipment in Forum) specific data'
1.4 |  | Pierre | Reviewed | Wording 'Asset' replaced per: 'Device'
1.5 |  | Pierre | Reviewed | New commodity List Usage List added
1.6 | 2019-08-02 | Pierre | Reviewed | Tab: 'LIST' added, giving a synthesis of all the metadata, & how these metadata are managed in FE and EPC App Previous Tab 'LIST' becomes DEVICE LIST', giving the details of the metadata per device DEVICE LIST: Column 'Commercial reference' added for the communicating devices (fulfiled, except for new PowerTag: UL/SquareD, Rope, 160A) DEVICE LIST: Column 'RFID' added for the communicating devices DEVICE LIST: Device 'Acti9 iOF+SD24 bottom connector' added
1.7 | 2019-09-02 | Pierre | Reviewed | DEVICE LIST: Column 'Commercial reference' for the communicating devices: : commercial references added for: UL/SquareD PowerTag E Frame (partial) UL/SquareD PowerTag QO UL/SquareD PowerTag PowerPact H,J,L UL/SquareD PowerTag PowerPact Q,B PowerTag Rope PowerTag 160A
1.8 | 2019-09-09 | Pierre | Reviewed | LIST: reviewed with Michel Pellet (evolutions added) LIST/DEVICE LIST: new metadata: Load Name
1.9 | 2019-09-27 | Pierre | Reviewed | DEVICE LIST: - 'Breaker Capacity' becomes 'Breaker Capacity List' - 'Curve Type - Protection Type' becomes 'Curve Type - Protection Type List' - 'Usage' becomes 'Usage List' - 'Load Name' becomes 'Load Name List'
2.0 | 2019-10-04 | Pierre | Reviewed | LIST: Column 'Data Type' added LIST: some new comments LIST: EPC App does not manage anymore the fields: - Site / Logo - Owner - Activity - Panel location / Building - Floor(tbc) - Load monitored area / Building - Floor LIST: EPC App does not edit anymore the Controller SN LIST: Panel Specific data: IP & IK added LIST: FE can edit: - Breaker capacity - Curve type Protection Type - Pole number - Breaker Category - Incomer (Flag) - Installation UP/DOWN - Phase sequence (tbc) - Pre-Alarm Ir (%) LIST: Controller Data: SN, FW, HW, are automatically retrieved DEVICE LIST: New devices: - PowerTag F160 (Square D) - Wireless OF/SD for compact NSX (Quazar) - 4 Functions Protection Quatro (aca AFDD) DEVICE LIST, Device removed (not commercialized): - PowerTag A9 M63 3P+W (A9MEM1544) 2ndary Lists: evolution of Usage List, creation of Commodity List
2.1 | 2019-11-15 | Pierre | Reviewed | LIST: Breaker Capacity: Comment removed: ''May be automatically retrireved'' LIST: Comment about phase sequence defined at the device level (PowerTag) DEVICE LIST: Device Type List & Current Rating List (In): SIMPLIFICATION DEVICE LIST: Phase Sequence: PDM ShortName ID added DEVICE LIST: Phase Sequence column fulfilled DEVICE LIST: Installation UP/DOWN column fulfilled DEVICE LIST: Pre-Alarm % column fulfilled LIST/DEVICE LIST/2ndary Lists: 'Load Name' replaced by 'Load Type List', Load Type List added in the '2ndary Lists' tab
2.2 | 2019-12-03 | Pierre | Reviewed | LIST: Panel: IP & IK removed DEVICE LIST: Devices added: - HeatTag UL, HeatTag LORA, HeaTag Sigfox - PowerTag MTZ - Acti 9 Quatro (detailed list with commercial references) DEVICE LIST: Devices frozen: - PowerTag 2P 208-240 QO 70-125 - PowerTag 3P 208-240 QO 70-125 - PowerTag 2P 480V EDB 70-125 - PowerTag 3P 480V EDB 70-125 - PowerTag PP-H 150 3P (NSX UL) - PowerTag PP-J 250 3P (NSX UL) - PowerTag PP-L 600 3P (NSX UL)
2.3 | 2020-01-10 | Pierre | Reviewed | LIST: Panel: 2 columns added: CEWS Container / CEWS Metadata LIST: Panel Type replaced per: Panel Range, Panel Model LIST: Controller Startup date: removed LIST: Device Startup Date no more managed in EPC App LIST: Panel Specific data: 'Standard' removed DEVICE LIST: Environmental sensor / HeatTag priority changed: 1 >>2 PREDEFINED EVENTS tab added: list of all the pre defined events sorted by Device familly
2.4 | 2020-02-14 | Pierre | Reviewed | PREDEFINED EVENTS: Voltage Loss (PowerTag): context is modified
2.5 | 2020-02-17 | Pierre Raulin + Michel Pellet | Reviewed | DEVICE LIST: Priority (column B) are now in link with the 'ESXP partner Led 2.x' versions (Q2 2020 / 2.0, Q3 2020 / 2.1 etc..) (Still to be validated: PowerTag NEMA/SquareD)
2.6.1 | 2020-03-18 | Pierre Raulin + Jean Noel Olphand | Reviewed | DEVICE LIST: Commercial Ref of PowerTag Square D are modified (PLT prefix as 'PowerLogicTag' instead of PT (PowerTag)) PREDEFINED EVENTS: Events relative to HeatTag added DEVICE LIST: HeatTag: possibility to configure the Device Name ('NA' removed) DEVICE LIST: HeatTag: NA for Device/Serial Number-Commercial Reference-Startup Date DEVICE LIST: 2DI Digital Inputs added (BPaS EPG400) DEVICE LIST: 2 data added for Digital Inputs: SIgnal Element (DI Status), Unity (DI Pulse Meter)
2.6 | 2020-05-07 | Pierre Raulin + Jean Noel Olphand | Reviewed | DEVICE LIST: Priorization Release (column B) DEVICE LIST: Wireless OF/SD for MCCB (NSX, NSXm, Powerpact B) added DEVICE LIST: HeatTag cable overheating sensor: Release (Model, Commercial Reference) PREDEFINED EVENTS: Events relative to HeatTag: Release
2.7 | 2020-08-20 | Pierre Raulin | Reviewed | PREDEFINED EVENTS: Events relative to PowerTag 2DI DEVICE LIST: Column A, content modified: family now in consistency with the PDM DEVICE LIST: Column C: new definition & content: ESXP SCOPE (Partner LED / End User LED) DEVICE LIST: PowerTag 2DI: Device type list & current rating list added DEVICE LIST: Column 'INCOMER (FLAG)' renamed: 'INCOMER-MAIN (FLAG)' DEVICE LIST: Column 'INCOMER-MAIN (FLAG)', the void cells are fulfilled with the values YES/NO DEVICE LIST: Column 'INCOMER-MAIN (FLAG)', PM & IEM PowerMeter are no more 'NA', this metadata is now required for these Devices DEVICE LIST: Sensor: Evolution of available metadata (columns K to U (Device aka Equipment))
2.8 |  | Pierre Raulin | Reviewed | LIST: A dedicated column added for NEC2020 Single Panel solution LIST / DEVICE LIST: 2 Metadata added for PowerTag Ambient (Sensor Position - Measured Point) LIST / DEVICE LIST: Pre-Alarm Ir % (for PowerTag): removed: it is not a context metadata DEVICE LIST: ESXP SCOPE (column B): SWOF & NEC2020 added DEVICE LIST: Usage, Load Type: fulfiled with 'NA' for Device not providing metering data for energy DEVICE LIST: A9 Arc (Quattro): list updated DEVICE LIST: Some Devices removed: EM4300, PM800, PowerTag PLTQ0125xP, PowerTag PLTPP125xP, DEVICE LIST: PowerTag for EDB Breakers: Com Ref updated DEVICE LIST: HeatTag: Device model updated DEVICE LIST: Sensor TH110, CL110: Metadata added DEVICE LIST: Pas Model = PAS600 DEVICE LIST: Ruby ATS becomes: Transfer Switch (family) - TransferPact (Range)
2.9 |  | Pierre Raulin | Reviewed | DEVICE LIST: Current Rating (In): no more list for Protection / Circuit Breaker equiped with µlogic (this data can be read from a register, no need to configure it)
2.10 |  | Pierre Raulin | Reviewed | LIST' becomes 'LIST SMS' 'LIST L&C' added (to be completed) DEVICE LIST: missing L&C Devices added DEVICE LIST: 4 additonnal columns: '- Connectivity EPC Desktop (AO) '- Can be discovered with EPC Desktop (AS) '- Can be configured with EPC Desktop (AT) '- Native integration in PME (AU) '- Native integration in PSO (AV) DEVICE LIST: Family column: filter improvements DEVICE LIST: PowerTag Rope & HR: metadata evolution (mounting position, phase sequence) DEVICE LIST: PowerTag A9, NSX: metadata evolution (mounting position) DEVICE LIST: PowerTag metadata: Power Supply / Positive Current Direction added DEVICE LIST: incomer-Main Flag: managed for all the PowerTag Energy (some were missing)
2.11 | 2020-10-13 | Pierre Raulin | Reviewed | DEVICE LIST: Some A9 Arc 'Quattro' reference are not available (put in orange color) DEVICE LIST: Gateway (PaS) / DI: Device model = PAS600L DEVICE LIST: PaS References: evolutions DEVICE LIST: Usage & Load Type List evolutions (wordings + additionnal Load Types for NEC2020)
2.12 | 2020-11-02 | Pierre Raulin | Reviewed | LIST / DEVICE LIST: 'System Type' metadata added (dedicated for PowerTag Rope/HR/NSX3P) DEVICE LIST: PowerTag Rope: Device Type List / Current Rating List fulfiled with 'NA' DEVICE LIST: Phase Sequence (phase order for PowerTag): evolution for 3 phase PowerTag products DEVICE LIST / 2ndary LIST: 2ndary List split in: Loads data List / Thermal Sensor data List DEVICE LIST / Therma Sensor data List: Improvement of the description for the data: Device Type List / Sensor Position / Measured Point
2.13 | 2020-11-20 | Pierre Raulin |  | DEVICE LIST: Usage added on PowerTag C 2DI & DIDO DEVICE LIST: Wireless OF/SD (aka ZAC, Quazar): some evolutions Thermal Sensor Data List: evolutions PREDEFINED EVENTS: Wireless OF/SD (aka ZAC-Quazar) added
2.14 | 2020-12-04 | Pierre Raulin |  | DEVICE LIST: A9 Arc (Quattro): Phase Sequence added DEVICE LIST: HeatTag Sensor: metadata added (Device Type, Sensor position, Measured point, Cubicle ID, Cubicle Type) DEVICE LIST: Device Type List is fulfilled even if there is only one Device Type DEVICE LIST: Curent Rating List is fulfilled even if there is only one Current Rating Load data List becomes: Data List Thermal Sensor Data List: evolutions PREDEFINED EVENTS: Short Name ID's evolution for Wireless OF/SD (ZAC) & PowerTag C 2DI
2.15 | 2020-12-18 | Pierre Raulin |  | LIST SMS: evolutions (details) LIST L&C: evolutions (details) PREDEFINED EVENTS: OF/SD/SDE Status event for Wireless OF/SD (ZAC): evolution PREDEFINED EVENTS: Battery Status event for Wireless OF/SD (ZAC) added
2.16 | 2021-01-05 | Pierre Raulin |  | DEVICE LIST: 'End User LED' Device parameters evolution ('NA' where needed). ('End User LED' Devices: see column B 'ESXP Scope') DEVICE LIST / PowerTag Rope: evolutions (Current Rating, Pole number, Phase Sequence) DEVICE LIST / PowerTag HR: evolutions (Com Ref NEMA, Device Type List, Pole Number) DEVICE LIST / Acti 9 A9 Arc (Quattro): Current Rating List: evolution Thermal Sensor data List: TH110: Sensor Positions added PREDEFINED EVENTS: Communication Loss event for Wireless OF/SD (ZAC) added PREDEFINED EVENTS: Communication Loss event for HeatTag added
2.17 | 2021-02-16 | Pierre Raulin |  | DEVICE LIST: monitored area (load) data (ZONE, USAGE…): Evolution DEVICE LIST Protection Device / A9 Arc (Quatro) / Com Ref A9xxx40 (add on): Evolution (Current Rating List) DEVICE LIST Protection Device / A9 Arc (Quatro): Evolution (Rated Voltage, Rated Frequency, Standard) DEVICE LIST Sensor / HeatTag: Evolution Thermal Sensor data List (for CTM Solution) / HeatTag: Evolution
2.18 | 2021-03-17 | Pierre Raulin |  | DEVICE LIST Protection Device / A9 Arc (Quatro): 'A9 Arc' replaced per 'A9 Active' DEVICE LIST Protection Device / A9 Arc (Quatro): Evolution (Communication protocol = Zigbee GP) DEVICE LIST Protection Device / A9 Arc (Quatro): Evolution (Curve Type) DEVICE LIST Protection Device / A9 Arc (Quatro): Evolution (Power Supply: Top / Bottom) DEVICE LIST: columns added: Feeder ID, Drawer ID: (for PowerTag Ambiant) DEVICE LIST: Wireless OF/SD auxiliary (ZAC): Incomer Flag: put in orange color (postponed) Thermal Sensor data list: TH110 / LV Switchboard / Sensor Position: 'Other' is added Thermal Sensor data list: TH110 / LV Switchboard / Sensor Position: legacy fields added (in orange color)
2.19 | 2021-04-02 | Pierre Raulin |  | DEVICE LIST Protection Device / A9 Active (Quatro): Evolution (Curve Type) Data List: Usage: evolution=alignment with PTI19 + Legacy Usage additional values (seperate) Data List: Load type: put in orange color, pending (in progress, ESXP MKT+PDM+EDMV2) PREDEFINED EVENTS: Battery Status events for Wireless OF/SD (ZAC): Evolution
2.20 | 2021-04-23 | Pierre Raulin |  | LIST SMS / LIST L&C: Column E ('Values') added: fulfiled with the List of Values defined at an upper level than Devices (eg: defined at Panel level) DEVICE LIST: Columns 'RATED VOLTAGE', 'RATED FREQUENCY', 'STANDARD' in gray color (no more to take into account at device level: configured at panel level) DEVICE LIST: PowerTag A9 Flex: Pole Number: evolution DEVICE LIST: Columns 'INCOMER-FLAG': postponed, this data is currently part of 'Legacy' Usage List (investigation in progress, ESXP MKT+PDM+EDMV2) Data List: Usage: evolution=alignment with PTI19 + Legacy Usage additional values (seperate) Data List: Load type: put in orange color, pending (investigation in progress, ESXP MKT+PDM+EDMV2)
2.21 | 2021-05-18 | Pierre Raulin |  | DEVICE LIST / PowerMeter / PowerTag A9 / DEVICE MODEL=A9 M63 / POLE NUMBER (of associate Breaker): evolutions for: 1P+W / 1P+N / 3P+N versions DEVICE LIST / PowerMeter / PowerTag A9 / DEVICE MODEL=A9 F63 / POLE NUMBER (of associate Breaker): evolutions DEVICE LIST / PowerMeter / PowerTag HR / POLE NUMBER (of associate Breaker): evolutions Thermal Sensor data list / HeatTag: 'None' added PREDEFINED EVENTS: 'Comm Loss' event added for all Zigbee Devices
2.22 | 2021-06-25 | Pierre Raulin |  | DEVICE LIST / Column B (ESXP SCOPE): distinction between SWOF IEC & SWOF NEMA added DEVICE LIST / Protection Device / A9 Active / POLE NUMBER=2P: PHASE SEQUENCE evolution DEVICE LIST / Protection Device Breaker / Device Range = 'BCM Wireless' added Data List / Usage List: 'None' added, + meaning of 'None' is precised Thermal Sensor data List: Cubicle Type for HeatTag: 'Incomer & Feeders' replaced per 'Incomer And Feeders' Thermal Sensor data List: meaning of 'None' is precised PREDEFINED EVENTS: Wireless OF/SD: Detection Rate evolution = 9*8h = 72h
2.23 | 2021-09-14 | Pierre Raulin |  | LIST SMS / LIST L&C / DEVICE LIST: 'Device Type' becomes 'Device Range', 'Device Type List' becomes 'Device Range List', 'Device Model' added LIST SMS / LIST L&C / DEVICE LIST: for all standalone products (eg PM, IEM...): 'Device Type' values are moved in 'Device Model' LIST SMS-L&C: Rated voltage range added DEVICE LIST / NEMA PowerLogicTag: evolution of values for mounting positions (Line / Load instead of Top / Bottom used for IEC Devices) DEVICE LIST / HeatTag NEMA: ESXP Scope evolution including SWOF NEMA DEVICE LIST / PowerTag A: 2 Ref: Eliwell & SE but with the same commercial reference = SE commercial reference DEVICE LIST / Transfer Switch / transferPact (Ruby): Com Ref added, Current ratings added, Pole number added PREDEFINED EVENTS: 'Standard Input' Events added for PowerTag C 2DI PREDEFINED EVENTS: Masterpact MTZ added
2.24 | 2021-10-14 | Pierre Raulin |  | DEVICE LIST / Power Meter / PowerLogicTag QO - PowerLogicTag E-Frame: Mounting Position = 'Load' / Power Supply = 'Line' or 'Load' DEVICE LIST / Protection Device - MV Relay Familly: BMM (Lego) device added DEVICE LIST / Gateway / ZBRN32 added (aka 'Sologate')
2.25 | 2021-11-26 | Pierre Raulin |  | DEVICE LIST / Power Meter / PowerTag-PowerLogicTag / Modbus Address Values = 1 to 247 DEVICE LIST / Power Meter / PowerLogicTag: Phase sequence: phase labels = A,B,C DEVICE LIST / Power Meter / PowerTag-PowerLogicTag / 'Power Supply' - 'Positive Current Direction' wordings replaced per: 'Current Flow' (values = 'Direct / Line' or 'Reverse / Load') DEVICE LIST / Power Meter / PowerTag-PowerLogicTag / 'Mounting position': values = 'Top / Line' or 'Bottom / Load' DEVICE LIST / Power Meter / PowerTag / A9: Current Rating List (In) evolution: '1,6A' removed, '13A' added DEVICE LIST / Power Meter / PowerTag / HR & Rope: Evolution of Minimum values for Current Rating (Ir) Thermal Sensor data list: TH110 & CL110 evolution of the parameters for CTM NEMA & LEGO needs Thermal Sensor data list: TH110 evolution of the parameters for CTM: -Missing Sensor positions for LV Switchboard = LV HBB VBB Joint / LV Splice Bar -Sensor Position for LV Switchboard added: LV Incomer Cable Connection 3&4
2.26 | 2022-01-11 | Pierre Raulin |  | LITS SMS, LIST L&C: Location parameters in consistency with PTI059 DEVICE LIST / Protection Device / A9 Active (Quattro): Current Flow values = Direct / Reverse DEVICE LIST / Protection Device/Breaker/BCM Wireless: Evolution: for µlogic P & H only DEVICE LIST / Protection Device - MV RelayCond.Monitoring Familly: BMM (Lego): Precisions on device identification: Range, Model, Com Ref + Familiy is changed = Cond.Monitoring Data List: Usage list is synchronized with the list managed by iOT Bridge: PTI019 values + 'Legacy' other values Thermal Sensor data list: TH110 & CL110 evolution of the parameters for CTM NEMA & LEGO & contextualization enhancements
2.27 | 2022-01-26 | Pierre Raulin |  | DEVICE LIST / Power Meter / PowerTag / A9 - NSX: Current Flow: 'Direct' replaced per 'Top', 'Reverse' replaced per 'Bottom' DEVICE LIST / Power Meter / PowerLogicTag / Q0 - E-Frame: Current Flow: 'Direct' replaced per 'Top', 'Reverse' replaced per 'Bottom' DEVICE LIST / Protection Device / A9 Active (Quattro): Current Flow values = 'Top/Line', 'Bottom/Load' Thermal Sensor data list: TH110 & CL110 evolution of the parameters for CTM NEMA & LEGO & contextualization: last evolutions after JAMA Review
2.28 | 2022-02-26 | Pierre Raulin |  | DEVICE LIST / Power Meter / PowerTag / A9 - NSX: Mounting Position: Top/Bottom DEVICE LIST / Power Meter / PowerTag / A9 - NSX: Power Supply: Top/Bottom DEVICE LIST / Power Meter / PowerLogicTag / Q0 - E-Frame: Mounting Position: Load DEVICE LIST / Power Meter / PowerLogicTag / Q0 - E-Frame: Power Supply: Line/Load DEVICE LIST / Power Meter / PowerTag / Rope - HR: Mounting Position: Top/Bottom DEVICE LIST / Power Meter / PowerTag / Rope - HR: Current Flow: Direct/Reverse DEVICE LIST / Power Meter / PowerLogicTag / Rope - HR: Mounting Position: Line/Load DEVICE LIST / Power Meter / PowerLogicTag / Rope - HR: Current Flow: Direct/Reverse DEVICE LIST / Protection Device / A9 Active (Quattro): Power Supply: Top/Bottom
2.29 | 2022-03-17 | Pierre Raulin |  | DEVICE LIST / Power Meter / PowerTag / NSX: Mounting Position: Bottom/Top (not only Bottom) DEVICE LIST / Protection Device: Smart RCD References added DEVICE LIST / Transfer Switch / transferPact (Ruby): Com Ref for 'Ruby Plus' added
2.30 | 2022-05-20 | Pierre Raulin |  | DEVICE LIST: column PDM FAMILY NAME added DEVICE LIST / Monitored Load Area: Building, Floor: not consider these 2 parameters for the moment (EDM Location Definition in progress) DEVICE LIST / Protection Device / A9 Active (Quattro): Current Rating List: Evolution: 13A value available for each reference DEVICE LIST / Protection Device / A9 Smart RCD: Current Rating List: Evolution: values < 6A removed + 13A value available for each reference DEVICE LIST / Protection Device / Vigilohm: commercial references added Thermal Sensor data List / HeatTag: Cubicle ID, Drawer ID evolutions. Sensor Position: 'Other' instead of 'None'. (In consistency with TH110-CL110)
2.31 | 2022-07-01 | Pierre Raulin |  | DEVICE LIST / Line 1 improvement for a better understanding of the different sections DEVICE LIST / 1 column added in 'Electrical Device (aka equiment in EDM) Specific Data' section = MEASURE TYPE LIST (CONTROL UNIT), to reflect the control unit measure type (eg: A,E,P,H) DEVICE LIST / Protection Device/Breaker/BCM Wireless: Evolution: Range, Commercial Reference added DEVICE LIST / Cond.Monitoring: GMM added DEVICE LIST / Cond.Monitoring: PD100 (PD Box vivaldi) added Thermal Sensor data List / TH110 / MV Cubicle: Circuit Breaker ID added for Sensor Position = BusBarConnection1,2 Thermal Sensor data List / CL110 / Measured Point evolution of one value: '3 Phases' instead of '3 Phase'
2.32 | 2022-07-06 | Pierre Raulin |  | DEVICE LIST / Column C (ESXP Scope): 'Partner' replaced per 'CIB', 'End User LED' replaced per 'Mission Critical' DEVICE LIST / Column C (ESXP Scope): SWOF IEC added for A9 Active Quattro & A9 Smart RCD
2.33 | 2022-08-16 | Pierre Raulin |  | DEVICE LIST / Protection Device / A9 Active (Quattro): reduction of the number of available references for SWOF IEC (column 'ESXP SCOPE') DEVICE LIST / Protection Device / A9 Smart RCD: reduction of the number of available references for SWOF IEC (column 'ESXP SCOPE')
2.34 | 2022-10-17 | Pierre Raulin |  | PREDEFINED EVENTS / Transfer Switch - TransferPact predefined events added DEVICE LIST / Commodity column: 'NA' replaced per 'No commodity' DEVICE LIST / DIGITAL INPUT TYPE (Signal Element) column added Data List / Commodity List Evolution Data List / digital input type (Signal Element) List added DEVICE LIST / EM4200 PowerMeter range added (required for CWP Scope, not natively integrated in PaS) DEVICE LIST / ION7550/7650 PowerMeter added (required for CWP Scope, not natively integrated in PaS)
2.35 | 2022-11-21 | Pierre Raulin |  | DEVICE LIST / Cond.Monitoring: GMM: Device Model evolution: PTM100 instead of TGM100 DEVICE LIST / Cond.Monitoring: PDBox: Equipment Type, Cubicle ID, Circuit Breaker ID added DEVICE LIST / Cond.Monitoring: MCM references added (MCM100 & MCM200) DEVICE LIST / Smartlink Modbus (Legacy): Evolution in consistency with PDM: PDM Family Name = IO Device / Range = Acti9 / Model = SmartLink DEVICE LIST / Smartlink Modbus (Refresh): 2 references added: Modbus, Modbus+Zigbee Data List Usage: new values added to cover energy codes management solutions: 'Electrical vehicle charging station', 'Water system pumps', 'Loads associated with renewable power source', 'Plug loads' Data List Usage value modified to be consistent with energy codes management solutions: 'Renewable power source' instead of 'Renewable Energy Production’ PREDEFINED EVENTS / A9 Active (Quattro & Smart RCD) predefined events added
2.36 | 2023-07-03 | Pierre Raulin |  | DEVICE LIST / Line 2: wording evolution: FRAME RATING instead of CURRENT RATING (reflects the Equipment (Breaker) Frame Rating)) DEVICE LIST / Line 2: add 2 columns: Ir CURRENT, Ir CURRENT LIST (reflects the current value above which the circuit breaker will trip) > Impacts: 1/ For the Ir pre-alarms Breaker Features: Ir CURRENT shall be considered (same values as the ones shown in the previous CURRENT RATING column). 3 cases: 1 Unique value (eg: some Acti9 Devices, as Quattro 'Standalone' products) or 1 list of values (eg: PowerTag) or Value automatically read (eg: Micrologic) 2/ For the Asset Management Features (to identify Breaker main characteristics): FRAME RATING shall be considered > Waiting for 'Composite Device management' for the management of this data DEVICE LIST / Ir CURRENT LIST evolution for: Power Meter / PowerTag / NSX, & HR

## LIST SMS
Metadata |  |  |  | Values | Data Type | CEWS Container Item | CEWS Metadata | Displayed on FE | Editable on FE | NEC 2020 | Displayed on EPC App | Editable on EPC App | Displayed on EPC Desktop | Editable on EPC desktop
Site |  |  | Comments
| Site name | Site | My Site Name, in link with invariant PTI059 |  | String | Panel | CommisionningHint | Y | Y | Y | Y | Y | Y | Y
| Site logo |  | MY Site Logo (picture jpg) |  | NA | NA | NA | Y | Y web portal | N | N | N | N | N
| Customer name |  |  |  | String | NA | NA | Y | Y | Y | N | N | N | N
| Activity |  |  |  | Enumerate/String | NA | NA | Y | Y | N | N | N | N | N
Site location:
|  | Address |  |  | String | NA | NA | Y | Y | Y | Y | Y | Y | Y
|  | GPS location | With EPC App only |  | String | NA | NA | Y | Y | Y | Y | Y | N | N
Panel (aka Switchboard / aka Enclosure)
| Name |  |  |  | String | Panel | Name | Y | Y | Y | Y | Y | Y | Y
| Standard |  |  | IEC NEMA | String | Panel |  | Y | Y | Y | Y | Y | Y | Y
| Type |  | Panel Range + Panel Model: eg: Prisma P |  | String | Panel | ProductRange + ProductModel | Y | Y | Y | Y | Y | Y | Y
| Serial Number |  | 'Virtual' Serial Number: editable or auto-generated |  | String | Panel |  | Y | Y | Y | Y | Y | Y | Y
| ID |  | Generated automatically from the information Type+Standard+SN, can be printed as a QR code (refer to 'Digital logbook story') |  | String / QR Code | Panel |  | Y | Y | Y | Y | Y | Y | Y
Panel Location:
|  | Building | Editable & Display in EPC but not in topology, in link with invariant PTI059 |  | String | Panel |  | Y | Y | Y | Y | Y | ? | ?
|  | Floor | Editable & Display in EPC but not in topology, in link with invariant PTI059 |  | String | Panel |  | Y | Y | Y | Y | Y | ? | ?
|  | Space | Logical Space for the installation, in link with invariant PTI059 (replace wording 'Zone') |  | String | Panel |  | Y | Y | Y | Y | Y | ? | ?
Panel Specific data:
|  | Rated Voltage | Value selection in a range | 100-690V | Integer | Panel | RatedVoltage | Y | Y | Y | Y | Y | ? | ?
|  | Rated Frequency |  | 50Hz 60Hz | Enumerate/Integer | Panel | RatedFrequency | Y | Y | Y | Y | Y | ? | ?
|  | Phase Sequence |  | 1-2-3 1-3-2 2-1-3 3-2-1 | Enumerate/String | Panel | RatedPhaseSequence | Y | Y | Y | Y | Y | ? | ?
|  | IP (Penetration Index) |  |  | Integer |  |  | N | N | N | N | N | N | N
|  | IK |  |  | Integer |  |  | N | N | N | N | N | N | N
Controller (aka Panel Server aka Gateway)
| Name |  |  |  | String | Device | Name | Y | Y | Y | Y | Y | Y | Y
| Location: | Building/Floor/Space | Populated from 'Panel', in link wiht invariant PTI059 |  | String |  |  | Y | N | Y | Y | N | Y | N
| Range |  | Automatically retrieved |  | String | Device | SerialNumber | Y | N | Y | Y | N | Y | N
| Model |  | Automatically retrieved |  | String | Device | SerialNumber | Y | N | Y | Y | N | Y | N
| Serial Number |  | Automatically retrieved |  | String | Device | SerialNumber | Y | N | Y | Y | N | Y | N
| FW Version |  | Automatically retrieved |  | String | Device | FirmwareVersion | Y | N | Y | Y | N | Y | N
| HW Version |  | Automatically retrieved |  | String | Device | HardwareVersion | Y | N | Y | Y | N | Y | N
| Startup date |  | Is the reference date for the Maintenance in FE |  | String |  |  | N | N | N | N | N | N | N
Device (aka Equipement)
| Name |  |  |  | String | Equipment | Name | Y | Y | Y | Y | Y | Y | Y
| Range |  | aka 'equipment' for TH110, CL110, SMT10020 (HeatTag) 'Standalone' Devices: automatically retrieved from the communicating part of the Device (eg: PM) End game for the other type of Devices: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String | Equipment | PoductRange | Y | N | Y | Y | Y | Y | Y
| Model |  | 'Standalone' Devices: automatically retrieved from the communicating part of the Device (eg: PM) End game for the other type of Devices: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String | Equipment | ProductModel | Y | N | Y | Y | Y | Y | Y
| Current Rating |  | For Breaker (In)- end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/Real |  |  | Y | N | Y | Y | Y | Y | Y
| Commodity |  | For Device which measure consumptions (WAGES) |  | Enumerate/String | Device | Commodity | Y | Y | Y | Y | Y | Y | Y
| Label |  |  |  | String |  |  | Y | Y | Y | Y | Y | Y | Y
| Serial number |  | editable or QR code flashing |  | String | Equipment | SerialNumber | Y | N | Y | Y | Y | Y | Y
| Commercial Reference |  | editable or QR code flashing |  | String | Equipment | CommercialReference | Y | N | Y | Y | Y | Y | Y
| Startup Date |  | Is the reference date for the Maintenance in FE |  | String |  |  | Y | Y | N | N | N | N | N
Load related Metadata:
|  | Usage | Usage of the load (eg: cooking) |  | Enumerate/String | Load | Usage | Y | Y | Y | Y | Y | Y | Y
|  | Type | Type of the load (eg: oven) |  | Enumerate/String | Load | Type | Y | Y | Y | Y | Y | Y | Y
|  | Building | tbc |  | String |  |  | Y | Y | Y | N | N | N | N
|  | Floor | tbc |  | String |  |  | Y | Y | Y | N | N | N | N
|  | Space | In link with invariant PTI059 (replace wording 'Zone') |  | String |  |  | Y | Y | Y | Y | Y | Y | Y
Communicating device related Metadata:
|  | Device Range | Retrieved automatically |  | String | Device | ProductRange | Y | N | Y | Y | N | Y | N
|  | Device Model | Retrieved automatically |  | String | Device | ProductModel | Y | N | Y | Y | N | Y | N
|  | Address (Modbus ID) |  |  | Integer |  |  | N | N | Y (End User LED) | Y | Y | Y | Y
|  | RF ID | Retrieved automatically |  | String |  |  | N | N | Y | Y | N | Y | N
|  | Serial Number | Retrieved automatically |  | String | Device | SerialNumber | Y | N | N | Y | N | Y | N
|  | Commercial Reference | Retrieved automatically |  | String | Device | CommercialReference | Y | N | Y | Y | N | Y | N
|  | FW revision | Retrieved automatically |  | String | Device | FirmwareVersion | Y | N | Y | Y | N | Y | N
Device Specific data:
|  | Breaker Capacity | end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String |  |  | Y | Y | N | Y | Y | Y | Y
|  | Curve Type Protection Type | May be retrieved automatically (from device) or end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String |  |  | Y | Y | N | Y | Y | Y | Y
|  | Pole Number | May be retrieved automatically (from device) or end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String |  |  | Y | Y | N | Y | Y | Y | Y
|  | Rated Voltage | Populated from 'Panel' |  | String |  |  | Y | N | Y | Y | N | Y | N
|  | Rated Frequency | Populated from 'Panel' |  | Enumerate/Integer |  |  | Y | N | Y | Y | N | Y | N
|  | Standard | Populated from 'Panel' |  | Enumerate/String |  |  | Y | N | Y | Y | N | Y | N
|  | Breaker Category | end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String |  |  | Y | Y | N | Y | Y | Y | Y
|  | Incomer-Main (Flag) |  |  | Boolean |  |  | Y | Y | Y | Y | Y | Y | Y
|  | Mounting Position | For PowerTag Energy |  | Enumerate/String | Device | IsUp | Y | Y | Y | Y | Y | Y | Y
|  | Power Supply | For PowerTag Energy (but not for Rope-HR) |  | Enumerate |  |  | ? | ? | Y (TBC) | N | N | Y | Y
|  | Positive Current Direction | For PowerTag Energy-Rope-HR |  | Enumerate |  |  | ? | ? | Y (TBC) | N | N | ? | ?
|  | Phase Sequence | For PowerTag Energy = do not confuse with 'Network' phase sequence defined at the Panel level Best wordings here would be: Connected Phase (single phase products) Connected Phases Order (3 phases products) |  | Enumerate/String | Equipment |  | Y | Y | Y | Y | Y | Y | Y
|  | Pre-Alarm Ir (%) | For PowerTag |  | Enumerate/Integer | Equipment | PreAlarm | Y | Y |  | Y | Y | Y | Y
|  | System Type | For PowerTag Energy-Rope-HR-NSX3P |  | Enumerate/String | Equipment |  | Y | Y | Y | Y | Y | Y | Y
|  | Sensor Position | For PowerTag Ambient (tbv if it could make sense for PowerTag Rope (?)) |  | Enumerate/String |  |  | N | N | N | Y | Y | Y | Y
|  | Measured Point | For PowerTag Ambient (tbv if it could make sense for PowerTag Rope (?)) |  | Enumerate/String |  |  | N | N | N | Y | Y | Y | Y
Note on B33: Not available in EPC
Note on C74: FE: To be investigated in a future wave or or for a new business oportunity
Note on C75: FE: To be investigated in a future wave or or for a new business oportunity

## LIST L&C
Metadata |  |  |  | Values | Data Type | EAA | NEC 2020 | Edge Solution | Displayed on EPC Desktop | Editable on EPC desktop
Site |  |  | Comments
| Site name | Site | My Site Name, in link with invariant PTI059 |  | String | Y | Y (TBC) | Y | Y | Y
| Market Segment |  |  |  | Enumerate | N | N | Y | Y | Y
| Contact Name |  | Customer Name |  | String | N | Y | Y | Y | Y
Adress (Site Location):
|  | Street |  |  | String | N | Y | Y | Y | Y
|  | City |  |  | String | N | Y | Y | Y | Y
|  | Zip Code |  |  | String | N | Y | Y | Y | Y
|  | Country |  |  | Enumerate | N | Y | Y | Y | Y
|  | State |  |  | Enumerate | N | Y | Y | Y | Y
|  | GPS location |  |  | String | N | N | N | N | N
Building
| Name | Building | Building Name, in link with invariant PTI059 |  | String | ? | ? | ? | Y | Y
Panel (aka Switchboard / aka Enclosure)
| Name |  |  |  | String | N | Y | Y | Y | Y
| Standard |  |  | IEC NEMA | Enumerate | N | Y | Y | Y | Y
| Type |  | Panel Range + Panel Model: eg: Prisma P |  | Enumerate | N | Y | Y | Y | Y
| Serial Number |  | 'Virtual' Serial Number: editable or auto-generated |  | String | N | Y | Y | Y | Y
| ID |  | Generated automatically from the information Type+Standard+SN, can be printed as a QR code (refer to 'Digital logbook story') |  | String / QR Code | N | Y | Y | Y | Y
Panel Location:
|  | Floor | Floor Name, in link with invariant PTI059 |  | String | ? | ? | ? | ? | ?
|  | Space | Space Name, in link with invariant PTI059 (replace wording: 'Zone') |  | String | Y | Y | Y | Y | Y
Panel Specific data:
|  | Rated Voltage | Value selection in a range | 100-690V | Integer | N | Y | Y | ? | ?
|  | Rated Frequency |  | 50Hz 60Hz | Enumerate/Integer | N | Y | Y | ? | ?
|  | Phase Sequence |  | 1-2-3 1-3-2 2-1-3 3-2-1 | Enumerate/String | N | Y | Y | ? | ?
Cubicle
| Cubicle name |  |  |  | String | ? | ? | ? | N | N
| Cubicle Standard |  | IEC or NEMA |  | Enumerate | ? | ? | ? | N | N
| Cubicle Type |  | Cubicle Range + Cubicle Model: (MV Ref) |  | Enumerate | ? | ? | ? | N | N
| Cubicle SN |  | 'Virtual' Serial Number: editable or auto-generated |  | String | ? | ? | ? | N | N
| Cubicle ID |  | Generated automatically from the information Type+Standard+SN, can be printed as a QR code (refer to 'Digital logbook story') |  | String / QR Code | ? | ? | ? | N | N
Cubicle location:
|  | Building | Populated from Building: 'Buiding Name' |  | String | ? | ? | ? | N | N
|  | Floor | Populated from Switchboard: 'Floor Name' |  | String | ? | ? | ? | N | N
|  | Space | Populated from Switchboard: 'Swichboard Name' |  | String | ? | ? | ? | N | N
Controller (aka Panel Server aka Gateway)
| Name |  |  |  | String | Y | Y | Y | Y | Y
| Range |  | Automatically retrieved |  | String | Y | Y | Y | Y | N
| Model |  | Automatically retrieved |  | String | Y | Y | Y | Y | N
| Serial Number |  | Automatically retrieved |  | String | Y | Y | Y | Y | N
| FW Version |  | Automatically retrieved |  | String | Y | Y | Y | Y | N
| HW Version |  | Automatically retrieved |  | String | Y | Y | Y | Y | N
| Location: | Zone | Populated from 'Panel' + 'Cubicle' |  | String | Y | Y | Y | Y | N
| Startup date |  | Is the reference date for the Maintenance in FE |  | String | N | N | N | N | N
Device (aka Equipement)
| Name |  |  |  | String | Y | Y | Y | Y | Y
| Range |  | aka 'equipment' for TH110, CL110, SMT10020 (HeatTag) 'Standalone' Devices: automatically retrieved from the communicating part of the Device (eg: PM) End game for the other type of Devices: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String | Y | Y | Y | Y | Y
| Model |  | 'Standalone' Devices: automatically retrieved from the communicating part of the Device (eg: PM) End game for the other type of Devices: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String | Y | Y | Y | Y | Y
| Current rating |  | For Breaker (In)- end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/Real | Y | Y | Y | Y | Y
| Commodity |  | For Device which measure consumptions (WAGES) |  | Enumerate/String | Y | Y | Y | N | N
| Label |  |  |  | String | Y | Y | Y | Y | Y
| Serial Number |  | editable or QR code flashing |  | String | Y | Y | Y | Y | Y
| Commercial Reference |  | editable or QR code flashing |  | String | Y | Y | Y | Y | Y
| Startup Date |  |  |  | String | Y | N | Y | N | N
Load related Metadata:
|  | Usage | Usage of the load (eg: cooking) |  | Enumerate/String | Y | Y | Y | Y | Y
|  | Type | Type of the load (eg: oven) |  | Enumerate/String | Y | Y | Y | Y | Y
|  | Building | tbc |  | String | Y | Y | Y | N | N
|  | Floor | tbc |  | String | Y | Y | Y | N | N
|  | Space | In link with invariant PTI059 (replace wording 'Zone') |  | String | Y | Y | Y | Y | Y
Communicating device related Metadata:
|  | Device Range | Retrieved automatically |  | String | Y | Y | Y | Y | N
|  | Device Model | Retrieved automatically |  | String | Y | Y | Y | Y | N
|  | Address (Modbus ID) |  |  | Integer | N | Y | Y | Y | Y
|  | RF ID | Retrieved automatically |  | String | N | Y | Y | Y | N
|  | Serial Number | Retrieved automatically |  | String | Y | N | Y | Y | N
|  | Commercial Reference | Retrieved automatically |  | String | Y | Y | Y | Y | N
|  | FW revision | Retrieved automatically |  | String | Y | Y | Y | Y | N
Device Specific data:
|  | Breaker Capacity | end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String | Y | N | Y | Y | Y
|  | Curve Type Protection Type | May be retrieved automatically (from device) or end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String | Y | N | Y | Y | Y
|  | Pole Number | May be retrieved automatically (from device) or end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String | Y | N | Y | Y | Y
|  | Rated Voltage | populated from 'Panel' |  | String | Y | Y | Y | Y | N
|  | Rated Frequency | populated from 'Panel' |  | Enumerate/Integer | Y | Y | Y | Y | N
|  | Standard | populated from 'Panel' |  | Enumerate/String | Y | Y | Y | Y | N
|  | Breaker Category | end game: automatically retrieved (from cloud) after QR code flashing (SN + Com Ref) |  | Enumerate/String | Y | N | Y | Y | Y
|  | Incomer-Main (Flag) |  |  | Boolean | Y | Y | Y | Y | Y
|  | Mounting position | For PowerTag Energy |  | Enumerate | Y | Y | Y | Y | Y
|  | Pre-Alarm Ir (%) | For PowerTag |  | Enumerate/Integer |  |  | Y | Y | Y
|  | Power Supply | For PowerTag Energy (but not for Rope-HR) |  | Enumerate | Y | Y | Y | Y | Y
|  | Positive Current Direction | For PowerTag Energy-Rope-HR |  | Enumerate | Y | Y | Y | ? | ?
|  | Phase Sequence | For PowerTag Energy = do not confuse with 'Network' phase sequence defined at the Panel level Best wordings here would be: Connected Phase (single phase products) Connected Phases Order (3 phases products) |  | Enumerate/String | Y | Y | Y | Y | Y
|  | System Type | For PowerTag Energy-Rope-HR-NSX3P |  | Enumerate/String | Y | Y | Y | Y | Y
|  | Sensor Position | For PowerTag Ambient, CTM Solutions |  | Enumerate/String | N | N | Y | Y | Y
|  | Measured Point | For PowerTag Ambient, CTM Solutions |  | Enumerate/String | N | N | Y | Y | Y
|  | Cubicle ID | For PowerTag Ambient, CTM Solutions |  | Enumerate/String | N | N | Y | Y | Y
|  | Cubicle Type | For PowerTag Ambient, CTM Solutions |  | Enumerate/String | N | N | Y | Y | Y
Note on B24: Not sure it is available in EPC...
Note on A28: New Level, may be useful for some Devices (eg HeatTag), and for MV
Note on B30: Make sense for MV Cubicle ? Tbc
Note on B31: Make sense for MV Cubicle ? Tbc
Note on B32: Make sense for MV Cubicle ? Tbc
Note on B33: Make sense for MV Cubicle ? Tbc
Note on B45: Not available in EPC
Note on C83: Available in EPC ?

## DEVICE LIST
General Information |  |  |  | Communicating Device Data | [6 empty] | Electrical Device (aka Equipment in EDM) data | [13 empty] | Electrical Device (aka Equipment in EDM) specific data | [9 empty] | Communicating Device specific data | [13 empty] | Monitored area (Load) data |  |  |  |  | Additional Information in the next columns >>>> |  | Can be discovered with EPC Desktop | Can be configured with EPC Desktop | Native Integration in PME | Native Integration in PSO | Conversion | IsNeutralAvailable | Out Of Scope of iOT Bridge
FAMILY | PDM FAMILY NAME | ESXP SCOPE | COMMUNICATION PROTOCOL | DEVICE RANGE | DEVICE MODEL | ADDRESS (MODBUS ID) | RF ID | SERIAL NUMBER | COMMERCIAL REFERENCE | FW REVISION | DEVICE RANGE | DEVICE RANGE LIST | DEVICE MODEL | DEVICE NAME (aka User Application Name) | Ir CURRENT (can be equal to 'In' on certain breaker range (eg Acti9)) | Ir CURRENT LIST (can be equal to 'In' on certain breaker range (eg Acti9)) | FRAME RATING (can be equal to 'In' on certain breaker range (eg Acti9)) | FRAME RATING LIST (can be equal to 'In' on certain breaker range (eg Acti9)) | LABEL (eg for breaker: 'Q1') | COMMODITY | COMMODITY LIST | SERIAL NUMBER | COMMERCIAL REFERENCE | STARTUP DATE | BREAKER CAPACITY LIST | CURVE TYPE PROTECTION TYPE LIST | MEASURE TYPE LIST (CONTROL UNIT) | POLE NUMBER | RATED VOLTAGE (DEFINED AT PANEL LEVEL) SEE TAB 'LIST SMS' | RATED FREQUENCY (DEFINED AT PANEL LEVEL) SEE TAB 'LIST SMS' | STANDARD (DEFINED AT PANEL LEVEL) SEE TAB 'LIST SMS' | BREAKER CATEGORY | DIGITAL INPUT TYPE (aka signal element) | INCOMER-MAIN (FLAG) POSTOPONED, CURRENTLY PART OF 'USAGE' | PHASE SEQUENCE (PowerTag Energy - A9 Arc) XYZ (PowerTag Rope-HR) | MOUNTING POSITION (PowerTag Energy) | POWER SUPPLY - CURRENT FLOW (ROPE, HR) | SYSTEM TYPE (PowerTag Energy) | SENSOR POSITION (PowerTag Ambient) | MEASURED POINT (PowerTag Ambient) | CUBICLE ID (PowerTag Ambient) | CUBICLE TYPE (PowerTag Ambient) | CIRCUIT BREAKER ID (PowerTag Ambient) | DRAWER ID (PowerTag Ambient) |  |  |  |  | BUILDING: POSTPONED (EDM Location Definition in progress) | FLOOR: POSTPONED (EDM Location Definition in progress) | ZONE | USAGE LIST | LOAD TYPE LIST |  | CONNECTIVITY EPC DESKTOP
0-PDM Short Name ID | LPHD1_Family |  |  | LPHD1_Range | LPHD1_Model | MBSL_LCCH1_Address |  | LPHD1_SerNum | LPHD1_ProductCode | LPHD1_FwRev |  |  |  | LPHD1_UserAppliName | LT_PTOC1_StrVal |  | LPHD1_ARtg LPHD1_CircuitProtectionRatingCurrent |  | LPHD1_CircuitID |  |  |  | LPHD1_ProductCode |  |  |  |  | LPHD1_PolesNum | LPHD1_VRtg |  |  |  | DiIn_GGIO1_xxx | [18 empty] | LPHD1_Usage
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM2000 | iEM2000T | NA | NA |  | A9MEM2000T |  | IEM2000 | IEM2000 | iEM2000T |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2000T |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM2000 | iEM2010 | NA | NA |  | A9MEM2010 |  | IEM2000 | IEM2000 | iEM2010 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2010 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM2000 | IEM2050 | NA | NA |  | A9MEM2050 |  | IEM2000 | IEM2000 | IEM2050 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2050 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM2000 | iEM2055 | NA | NA |  | A9MEM2055 |  | IEM2000 | IEM2000 | iEM2055 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2055 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM2000 | iEM2105 | NA | NA |  | A9MEM2105 |  | IEM2000 | IEM2000 | iEM2105 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2105 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM2000 | iEM2110 | NA | NA |  | A9MEM2110 |  | IEM2000 | IEM2000 | iEM2110 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2110 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3110 | NA | NA |  | A9MEM3110 |  | IEM3000 | IEM3000 | iEM3110 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3110 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3135 | NA | NA |  | A9MEM3135 |  | IEM3000 | IEM3000 | iEM3135 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3135 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3155 | NA | NA |  | A9MEM3155 |  | IEM3000 | IEM3000 | iEM3155 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3155 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3210 | NA | NA |  | A9MEM3210 |  | IEM3000 | IEM3000 | iEM3210 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3210 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3235 | NA | NA |  | A9MEM3235 |  | IEM3000 | IEM3000 | iEM3235 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3235 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3255 | NA | NA |  | A9MEM3255 |  | IEM3000 | IEM3000 | iEM3255 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3255 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3310 | NA | NA |  | A9MEM3310 |  | IEM3000 | IEM3000 | iEM3310 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3310 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3355 | NA | NA |  | A9MEM3355 |  | IEM3000 | IEM3000 | iEM3355 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3355 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3455 | NA | NA |  | A9MEM3455 |  | IEM3000 | IEM3000 | iEM3455 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3455 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | digital I/O | IEM3000 | iEM3555 | NA | NA |  | A9MEM3555 |  | IEM3000 | IEM3000 | iEM3555 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3555 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM2000 | iEM2050 |  | NA |  | A9MEM2050 |  | IEM2000 | IEM2000 | iEM2050 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2050 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM2000 | iEM2055 |  | NA |  | A9MEM2055 |  | IEM2000 | IEM2000 | iEM2055 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2055 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM2000 | iEM2150 |  | NA |  | A9MEM2150 |  | IEM2000 | IEM2000 | iEM2150 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2150 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM2000 | iEM2155 |  | NA |  | A9MEM2155 |  | IEM2000 | IEM2000 | iEM2155 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM2155 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM3000 | iEM3150 |  | NA |  | A9MEM3150 |  | IEM3000 | IEM3000 | iEM3150 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3150 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM3000 | iEM3155 |  | NA |  | A9MEM3155 |  | IEM3000 | IEM3000 | iEM3155 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3155 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM3000 | iEM3250 |  | NA |  | A9MEM3250 |  | IEM3000 | IEM3000 | iEM3250 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3250 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM3000 | iEM3255 |  | NA |  | A9MEM3255 |  | IEM3000 | IEM3000 | iEM3255 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3255 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM3000 | iEM3350 |  | NA |  | A9MEM3350 |  | IEM3000 | IEM3000 | iEM3350 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3350 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM3000 | iEM3355 |  | NA |  | A9MEM3355 |  | IEM3000 | IEM3000 | iEM3355 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3355 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM3000 | iEM3455 |  | NA |  | A9MEM3455 |  | IEM3000 | IEM3000 | iEM3455 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3455 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / IEM | Power Meter | CIB + Mission Critical | Modbus SL | IEM3000 | iEM3555 |  | NA |  | A9MEM3555 |  | IEM3000 | IEM3000 | iEM3555 |  | NA | NA | NA | NA |  | Electricity | NA |  | A9MEM3555 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / EM43xx | Power Meter | Not supported by iOT Bridge | Zigbee Pro | EM4000 | EM4300 | NA |  |  | EM4300 |  | EM4000 | EM4000 | EM4300 |  | NA | NA | NA | NA |  | Electricity | NA |  | EM4000 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | ?
Power Meter / EM43xx | Power Meter | Not supported by iOT Bridge | Zigbee Pro | EM4000 | EM4399 | NA |  |  | EM4399 |  | EM4000 | EM4000 | EM4399 |  | NA | NA | NA | NA |  | Electricity | NA |  | EM4000 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | ?
Power Meter / PM | Power Meter | CIB + Mission Critical | digital I/O | PM3000 | PM3210 | NA | NA |  | METSEPM3210 |  | PM3000 | PM3000 | PM3210 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM3210 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / PM | Power Meter | CIB + Mission Critical | digital I/O | PM3000 | PM3250 | NA | NA |  | METSEPM3250 |  | PM3000 | PM3000 | PM3250 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM3250 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / PM | Power Meter | CIB + Mission Critical | digital I/O | PM3000 | PM3255 | NA | NA |  | METSEPM3255 |  | PM3000 | PM3000 | PM3255 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM3255 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / PM | Power Meter | CIB + Mission Critical | digital I/O | PM5000 | PM5100 | NA | NA |  | METSEPM5100 |  | PM5000 | PM5000 | PM5100 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5100 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / PM | Power Meter | CIB + Mission Critical | digital I/O | PM5000 | PM5110 | NA | NA |  | METSEPM5110 |  | PM5000 | PM5000 | PM5110 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5110 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / PM | Power Meter | CIB + Mission Critical | digital I/O | PM5000 | PM5111 | NA | NA |  | METSEPM5111 |  | PM5000 | PM5000 | PM5111 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5111 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / PM | Power Meter | CIB + Mission Critical | Modbus SL | PM3000 | PM3250 |  | NA |  | METSEPM3250 |  | PM3000 | PM3000 | PM3250 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM3250 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | CIB + Mission Critical | Modbus SL | PM3000 | PM3255 |  | NA |  | METSEPM3255 |  | PM3000 | PM3000 | PM3255 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM3255 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | CIB + Mission Critical | Modbus SL | PM5000 | PM5110 |  | NA |  | METSEPM5110 |  | PM5000 | PM5000 | PM5110 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5110 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | CIB + Mission Critical | Modbus SL | PM5000 | PM5111 |  | NA |  | METSEPM5111 |  | PM5000 | PM5000 | PM5111 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5111 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5310 |  | NA |  | METSEPM5310 |  | PM5000 | PM5000 | PM5310 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5310 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5310R |  | NA |  | METSEPM5310R |  | PM5000 | PM5000 | PM5310R |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5310R |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5320 |  | NA |  | METSEPM5320 |  | PM5000 | PM5000 | PM5320 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5320 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5320R |  | NA |  | METSEPM5320R |  | PM5000 | PM5000 | PM5320R |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5320R |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5330 |  | NA |  | METSEPM5330 |  | PM5000 | PM5000 | PM5330 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5330 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5331 |  | NA |  | METSEPM5331 |  | PM5000 | PM5000 | PM5331 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5331 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5340 |  | NA |  | METSEPM5340 |  | PM5000 | PM5000 | PM5340 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5340 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5341 |  | NA |  | METSEPM5341 |  | PM5000 | PM5000 | PM5341 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5341 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5350 |  | NA |  | METSEPM5350 |  | PM5000 | PM5000 | PM5350 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5350 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5350P |  | NA |  | METSEPM5350P |  | PM5000 | PM5000 | PM5350P |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5350P |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5350IB |  | NA |  | METSEPM5350IB |  | PM5000 | PM5000 | PM5350IB |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5350IB |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5350PB |  | NA |  | METSEPM5350PB |  | PM5000 | PM5000 | PM5350PB |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5350PB |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5560 |  | NA |  | METSEPM5560 |  | PM5000 | PM5000 | PM5560 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5560 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5560 |  | NA |  | METSEPM5560 |  | PM5000 | PM5000 | PM5560 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5560 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5561 |  | NA |  | METSEPM5561 |  | PM5000 | PM5000 | PM5561 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5561 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5561 |  | NA |  | METSEPM5561 |  | PM5000 | PM5000 | PM5561 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5561 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5562 |  | NA |  | METSEPM5562 |  | PM5000 | PM5000 | PM5562 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5562 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5562 |  | NA |  | METSEPM5562 |  | PM5000 | PM5000 | PM5562 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5562 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5562MC |  | NA |  | METSEPM5562MC |  | PM5000 | PM5000 | PM5562MC |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5562MC |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5562MC |  | NA |  | METSEPM5562MC |  | PM5000 | PM5000 | PM5562MC |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5562MC |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5563 |  | NA |  | METSEPM5563 |  | PM5000 | PM5000 | PM5563 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5563 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5563 |  | NA |  | METSEPM5563 |  | PM5000 | PM5000 | PM5563 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5563 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5570 |  | NA |  | METSEPM5570 |  | PM5000 | PM5000 | PM5570 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5570 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5570 |  | NA |  | METSEPM5570 |  | PM5000 | PM5000 | PM5570 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5570 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5580 |  | NA |  | METSEPM5580 |  | PM5000 | PM5000 | PM5580 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5580 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5580 |  | NA |  | METSEPM5580 |  | PM5000 | PM5000 | PM5580 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5580 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5650 |  | NA |  | METSEPM5650 |  | PM5000 | PM5000 | PM5650 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5650 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5650 |  | NA |  | METSEPM5650 |  | PM5000 | PM5000 | PM5650 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5650 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5660 |  | NA |  | METSEPM5660 |  | PM5000 | PM5000 | PM5660 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5660 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5660 |  | NA |  | METSEPM5660 |  | PM5000 | PM5000 | PM5660 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5660 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5661 |  | NA |  | METSEPM5661 |  | PM5000 | PM5000 | PM5661 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5661 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5661 |  | NA |  | METSEPM5661 |  | PM5000 | PM5000 | PM5661 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5661 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM5000 | PM5761 |  | NA |  | METSEPM5761 |  | PM5000 | PM5000 | PM5761 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5761 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM5000 | PM5761 |  | NA |  | METSEPM5761 |  | PM5000 | PM5000 | PM5761 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM5761 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Power Meter / PM | Power Meter | Not supported by iOT Bridge | Modbus SL | PM800 | PM810 |  | NA |  |  |  | PM800 | PM800 | PM810 |  | NA | NA | NA | NA |  | Electricity | NA |  | 0 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | ?
Power Meter / PM | Power Meter | Not supported by iOT Bridge | Modbus SL | PM800 | PM820 |  | NA |  | 15211 |  | PM800 | PM800 | PM820 |  | NA | NA | NA | NA |  | Electricity | NA |  | 15211 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | ?
Power Meter / PM | Power Meter | Not supported by iOT Bridge | Modbus SL | PM800 | PM850 |  | NA |  | 15212 |  | PM800 | PM800 | PM850 |  | NA | NA | NA | NA |  | Electricity | NA |  | 15212 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | ?
Power Meter / PM | Power Meter | Not supported by iOT Bridge | Modbus SL | PM800 | PM870 |  | NA |  | 15213 |  | PM800 | PM800 | PM870 |  | NA | NA | NA | NA |  | Electricity | NA |  | 15213 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | ?
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM8240 |  | NA |  | METSEPM8240 |  | PM8000 | PM8000 | PM8240 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8240 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM8210 |  | NA |  | METSEPM8210 |  | PM8000 | PM8000 | PM8210 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8210 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM8243 |  | NA |  | METSEPM8243 |  | PM8000 | PM8000 | PM8243 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8243 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM8213 |  | NA |  | METSEPM8213 |  | PM8000 | PM8000 | PM8213 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8213 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM8244 |  | NA |  | METSEPM8244 |  | PM8000 | PM8000 | PM8244 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8244 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM8214 |  | NA |  | METSEPM8214 |  | PM8000 | PM8000 | PM8214 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8214 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM82401 |  | NA |  | METSEPM82401 |  | PM8000 | PM8000 | PM82401 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM82401 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM82403 |  | NA |  | METSEPM82403 |  | PM8000 | PM8000 | PM82403 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM82403 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | PM8000 | PM82404 |  | NA |  | METSEPM82404 |  | PM8000 | PM8000 | PM82404 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM82404 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM8240 |  | NA |  | METSEPM8240 |  | PM8000 | PM8000 | PM8240 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8240 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM8210 |  | NA |  | METSEPM8210 |  | PM8000 | PM8000 | PM8210 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8210 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM8243 |  | NA |  | METSEPM8243 |  | PM8000 | PM8000 | PM8243 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8243 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM8213 |  | NA |  | METSEPM8213 |  | PM8000 | PM8000 | PM8213 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8213 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM8244 |  | NA |  | METSEPM8244 |  | PM8000 | PM8000 | PM8244 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8244 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM8214 |  | NA |  | METSEPM8214 |  | PM8000 | PM8000 | PM8214 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM8214 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM82401 |  | NA |  | METSEPM82401 |  | PM8000 | PM8000 | PM82401 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM82401 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM82403 |  | NA |  | METSEPM82403 |  | PM8000 | PM8000 | PM82403 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM82403 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | PM8000 | PM82404 |  | NA |  | METSEPM82404 |  | PM8000 | PM8000 | PM82404 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEPM82404 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | ION9000 | ION92030 |  | NA |  | METSEION92030 |  | ION9000 | ION9000 | ION92030 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION92030 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | ION9000 | ION92040 |  | NA |  | METSEION92040 |  | ION9000 | ION9000 | ION92040 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION92040 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | ION9000 | ION93030 |  | NA |  | METSEION93030 |  | ION9000 | ION9000 | ION93030 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION93030 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | ION9000 | ION93040 |  | NA |  | METSEIONI93040 |  | ION9000 | ION9000 | ION93040 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEIONI93040 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | ION9000 | ION95030 |  | NA |  | METSEION95030 |  | ION9000 | ION9000 | ION95030 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION95030 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus SL | ION9000 | ION95040 |  | NA |  | METSEION95040 |  | ION9000 | ION9000 | ION95040 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION95040 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | ION9000 | ION92030 |  | NA |  | METSEION92030 |  | ION9000 | ION9000 | ION92030 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION92030 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | ION9000 | ION92040 |  | NA |  | METSEION92040 |  | ION9000 | ION9000 | ION92040 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION92040 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | ION9000 | ION93030 |  | NA |  | METSEION93030 |  | ION9000 | ION9000 | ION93030 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION93030 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | ION9000 | ION93040 |  | NA |  | METSEIONI93040 |  | ION9000 | ION9000 | ION93040 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEIONI93040 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | ION9000 | ION95030 |  | NA |  | METSEION95030 |  | ION9000 | ION9000 | ION95030 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION95030 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / PM | Power Meter | Mission Critical | Modbus/TCP | ION9000 | ION95040 |  | NA |  | METSEION95040 |  | ION9000 | ION9000 | ION95040 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEION95040 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES (Basics)
Power Meter / BCPM | Power Meter | Mission Critical | Modbus SL | BCPMA | BCPMAxxx |  | NA |  | BCPMAxxx |  | BCPMA | BCPMA | BCPMAxxx |  | NA | NA | NA | NA |  | Electricity | NA |  | BCPMAxxx |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / BCPM | Power Meter | Mission Critical | Modbus/TCP | BCPME | BCPMEyyy |  | NA |  | BCPMEyyy |  | BCPME | BCPME | BCPMEyyy |  | NA | NA | NA | NA |  | Electricity | NA |  | BCPMEyyy |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / BCPM | Power Meter | Mission Critical | Modbus SL | BCPMSC | BCPMSCAxxx |  | NA |  | BCPMSCAxxx |  | BCPMSC | BCPMSC | BCPMSCAxxx |  | NA | NA | NA | NA |  | Electricity | NA |  | BCPMSCAxxx |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / BCPM | Power Meter | Mission Critical | Modbus SL | BCPMSC | BCPMSCByyy |  | NA |  | BCPMSCByyy |  | BCPMSC | BCPMSC | BCPMSCByyy |  | NA | NA | NA | NA |  | Electricity | NA |  | BCPMSCByyy |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / BCPM | Power Meter | Mission Critical | Modbus SL | BCPMSC | BCPMSCCzzz |  | NA |  | BCPMSCCzzz |  | BCPMSC | BCPMSC | BCPMSCCzzz |  | NA | NA | NA | NA |  | Electricity | NA |  | BCPMSCCzzz |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / BCPM | Power Meter | Mission Critical | Modbus/TCP | BCPMSC | BCPMSCEvvv |  | NA |  | BCPMSCEvvv |  | BCPMSC | BCPMSC | BCPMSCEvvv |  | NA | NA | NA | NA |  | Electricity | NA |  | BCPMSCEvvv |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4000 | Power Meter | Mission Critical | Modbus SL | EM4000 | EM4033 |  | NA |  | METSEEM403316 |  | EM4000 | EM4000 | EM4033 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM403316 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / EM4000 | Power Meter | Mission Critical | Modbus SL | EM4000 | EM4033 |  | NA |  | METSEEM403336 |  | EM4000 | EM4000 | EM4033 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM403336 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / EM4000 | Power Meter | Mission Critical | Modbus/TCP | EM4000 | EM4033 |  | NA |  | METSEEM403316 |  | EM4000 | EM4000 | EM4033 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM403316 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4000 | Power Meter | Mission Critical | Modbus/TCP | EM4000 | EM4033 |  | NA |  | METSEEM403336 |  | EM4000 | EM4000 | EM4033 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM403336 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4000 | Power Meter | Mission Critical | Modbus SL | EM4000 | EM4080 |  | NA |  | METSEEM408016 |  | EM4000 | EM4000 | EM4080 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM408016 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / EM4000 | Power Meter | Mission Critical | Modbus SL | EM4000 | EM4080 |  | NA |  | METSEEM408036 |  | EM4000 | EM4000 | EM4080 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM408036 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | NO
Power Meter / EM4000 | Power Meter | Mission Critical | Modbus/TCP | EM4000 | EM4080 |  | NA |  | METSEEM408016 |  | EM4000 | EM4000 | EM4080 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM408016 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4000 | Power Meter | Mission Critical | Modbus/TCP | EM4000 | EM4080 |  | NA |  | METSEEM408036 |  | EM4000 | EM4000 | EM4080 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM408036 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4235 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4235 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4236 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4236 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4235A12 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4235A12 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4235A18 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4235A18 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4235B101 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4235B101 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4235B201 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4235B201 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4235B401 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4235B401 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4236A12 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4236A12 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4236A18 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4236A18 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4236B101 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4236B101 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4236B201 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4236B201 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / EM4200 | Power Meter | Mission Critical | Modbus/SL | EM4200 | EM4200 |  | NA |  | METSEEM4236B401 |  | EM4200 | EM4200 | EM4200 |  | NA | NA | NA | NA |  | Electricity | NA |  | METSEEM4236B401 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / ION7550 | Power Meter | Mission Critical | Modbus/TCP | ION7500 | ION7550 |  | NA |  | 7550 |  | ION7500 | ION7500 | ION7550 |  | NA | NA | NA | NA |  | Electricity | NA |  | 7550 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / ION7650 | Power Meter | Mission Critical | Modbus/TCP | ION7600 | ION7650 |  | NA |  | 7650 |  | ION7600 | ION7600 | ION7650 |  | NA | NA | NA | NA |  | Electricity | NA |  | 7650 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | NO
Power Meter / PowerTag / A9 |  |  |  | PowerTags I60, M63 | [28 empty] | NA
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 M63 1P+W | 1---247 |  |  | A9MEM1520 |  |  | Acti 9 Reflex iC60 Acti 9 iKQE RCBO Multi 9 C60 Multi 9 ID Multi 9 C32N Multi 9 C65 Acti 9 iID Acti 9 iID K Acti 9 iK60 Acti 9 iKQ Acti 9 K60 Acti 9 iC65 Acti 9 DT60 Acti 9 iC60 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 1P 1P+N 2P | NA | NA | NA | NA | NA | YES NO | 1 2 3 | Top Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | SWAPB | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 M63 1P+N Top | 1---247 |  |  | A9MEM1521 |  |  | Acti 9 Reflex iC60 Acti 9 iKQE RCBO Multi 9 C60 Multi 9 ID Multi 9 C32N Multi 9 C65 Acti 9 iID Acti 9 iID K Acti 9 iK60 Acti 9 iKQ Acti 9 K60 Acti 9 iC65 Acti 9 DT60 Acti 9 iC60 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 1P+N 2P | NA | NA | NA | NA | NA | YES NO | 1 2 3 | Top | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | yes
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 M63 1P+N Bottom | 1---247 |  |  | A9MEM1522 |  |  | Acti 9 Reflex iC60 Acti 9 iKQE RCBO Multi 9 C60 Multi 9 ID Multi 9 C32N Multi 9 C65 Acti 9 iID Acti 9 iID K Acti 9 iK60 Acti 9 iKQ Acti 9 K60 Acti 9 iC65 Acti 9 DT60 Acti 9 iC60 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 1P+N 2P | NA | NA | NA | NA | NA | YES NO | 1 2 3 | Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | yes
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 M63 3P | 1---247 |  |  | A9MEM1540 |  |  | Acti 9 Reflex iC60 Acti 9 iKQE RCBO Multi 9 C60 Multi 9 ID Multi 9 C32N Multi 9 C65 Acti 9 iID Acti 9 iID K Acti 9 iK60 Acti 9 iKQ Acti 9 K60 Acti 9 iC65 Acti 9 DT60 Acti 9 iC60 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Top Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | SWAPB | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical | Zigbee GP | PowerTag | A9 M63 3P 230V VLL | 1---247 |  |  | A9MEM1543 |  |  | Acti 9 Reflex iC60 Acti 9 iKQE RCBO Multi 9 C60 Multi 9 ID Multi 9 C32N Multi 9 C65 Acti 9 iID Acti 9 iID K Acti 9 iK60 Acti 9 iKQ Acti 9 K60 Acti 9 iC65 Acti 9 DT60 Acti 9 iC60 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Top Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | SWAPB | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 M63 3P+N Top | 1---247 |  |  | A9MEM1541 |  |  | Acti 9 Reflex iC60 Acti 9 iKQE RCBO Multi 9 C60 Multi 9 ID Multi 9 C32N Multi 9 C65 Acti 9 iID Acti 9 iID K Acti 9 iK60 Acti 9 iKQ Acti 9 K60 Acti 9 iC65 Acti 9 DT60 Acti 9 iC60 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P+N 4P | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Top | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | yes
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 M63 3P+N Bottom | 1---247 |  |  | A9MEM1542 |  |  | Acti 9 Reflex iC60 Acti 9 iKQE RCBO Multi 9 C60 Multi 9 ID Multi 9 C32N Multi 9 C65 Acti 9 iID Acti 9 iID K Acti 9 iK60 Acti 9 iKQ Acti 9 K60 Acti 9 iC65 Acti 9 DT60 Acti 9 iC60 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P+N 4P | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | yes
Power Meter / PowerTag / A9 |  |  |  | PowerTags P63 (DT40…) | [28 empty] | NA
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 P63 1P+N Top | 1---247 |  |  | A9MEM1561 |  |  | Acti 9 iDPN Acti 9 iDPN (China version) Acti 9 iDPN Vigi Acti 9 DT40 Acti 9 DT40 Vigi Acti 9 C40 Acti 9 C40 Vigi Acti 9 iC40 Acti 9 iCV40 Multi 9 N40 Multi 9 N40 Vigi Acti 9 IDc Acti 9 ID C40 Acti 9 ITG40 DuoLine D'clic XP DuoLine ID'clic XP DuoLine D'clic Vigi Domae MCB Domae RCBO |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 1P+N | NA | NA | NA | NA | NA | YES NO | 1 2 3 | Top | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 P63 1P+N Bottom | 1---247 |  |  | A9MEM1562 |  |  | Acti 9 iDPN Acti 9 iDPN (China version) Acti 9 iDPN Vigi Acti 9 DT40 Acti 9 DT40 Vigi Acti 9 C40 Acti 9 C40 Vigi Acti 9 iC40 Acti 9 iCV40 Multi 9 N40 Multi 9 N40 Vigi DuoLine D'clic XP DuoLine D'clic Vigi Domae MCB Domae RCBO Acti 9 Vigi iDPN Acti 9 Vigi DT40 Acti 9 Vigi C40 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 1P+N | NA | NA | NA | NA | NA | YES NO | 1 2 3 | Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 P63 1P+N Bottom RCBO | 1---247 |  |  | A9MEM1563 |  |  | Acti 9 iKQE RCBO Acti 9 iC60 iC60H RCBO Acti 9 iC60 iC60H2 RCBO |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 1P+N | NA | NA | NA | NA | NA | YES NO | 1 2 3 | Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 P63 3P+N Top | 1---247 |  |  | A9MEM1571 |  |  | Acti 9 iDPN Acti 9 iDPN Vigi Acti 9 DT40 Acti 9 DT40 Vigi Acti 9 C40 Acti 9 C40 Vigi Acti 9 iC40 Acti 9 iCV40 Multi 9 N40 Multi 9 N40 Vigi |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P+N | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Top | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 P63 3P+N Bottom | 1---247 |  |  | A9MEM1572 |  |  | Acti 9 iDPN Acti 9 DT40 Acti 9 C40 Acti 9 iC40 Multi 9 N40 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P+N | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT
Power Meter / PowerTag / A9 |  |  |  | PowerTags Flex (aca DT40+Vigi), F63 | [28 empty] | NA
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 F63 1P+N | 1---247 |  |  | A9MEM1560 |  |  | Acti 9 Vigi iC60 Acti 9 iCV40 Acti 9 Vigi iC40 Acti 9 iDD40 XA Acti 9 iCV40 XA Acti 9 Vigi iDT40 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 1P+N | NA | NA | NA | NA | NA | YES NO | 1 2 3 | Top Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical | Zigbee GP | PowerTag | A9 F63 1P+N 110V | 1---247 |  |  | A9MEM1564 |  |  | Acti 9 Vigi iC60 Acti 9 iCV40 Acti 9 Vigi iC40 Acti 9 iDD40 XA Acti 9 iCV40 XA Acti 9 Vigi iDT40 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 1P+N | NA | NA | NA | NA | NA | YES NO | 1 2 3 | Top Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 F63 3P | 1---247 |  |  | A9MEM1573 |  |  | Acti 9 Vigi iC60 Acti 9 iCV40 Acti 9 Vigi iDPN Acti 9 Vigi DT40 Acti 9 Vigi C40 Acti 9 Vigi iC40 Acti 9 Vigi N40 Acti 9 iDD40 XA Acti 9 iCV40 XA Acti 9 Vigi iDT40 Acti 9 iDD40 Acti 9 Vigi iTG40 Acti 9 Vigi iCG40 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Top Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | A9 F63 3P+N | 1---247 |  |  | A9MEM1570 |  |  | Acti 9 Vigi iC60 Acti 9 iCV40 Acti 9 Vigi iDPN Acti 9 Vigi DT40 Acti 9 Vigi C40 Acti 9 Vigi iC40 Acti 9 Vigi N40 Acti 9 iDD40 XA Acti 9 iCV40 XA Acti 9 Vigi iDT40 Acti 9 iDD40 Acti 9 Vigi iTG40 Acti 9 Vigi iCG40 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P+N | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Top Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / A9 | Power Meter | CIB + Mission Critical | Zigbee GP | PowerTag | A9 F63 3P+N 110/230V | 1---247 |  |  | A9MEM1574 |  |  | Acti 9 Vigi iC60 Acti 9 iCV40 Acti 9 Vigi iDPN Acti 9 Vigi DT40 Acti 9 Vigi C40 Acti 9 Vigi iC40 Acti 9 Vigi N40 Acti 9 iDD40 XA Acti 9 iCV40 XA Acti 9 Vigi iDT40 Acti 9 iDD40 Acti 9 Vigi iTG40 Acti 9 Vigi iCG40 |  |  |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | 1A 2A 3A 4A 5A 6A 10A 13A 16A 20A 25A 32A 40A 50A 63A |  | Electricity | NA |  |  |  | NA | B C D | NA | 3P+N | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Top Bottom | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | VigiARC iC40 | 1---247 |  |  | A9TYBE625 |  | Acti9 iC40 | Acti9 iC40 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | VigiARC iC40 | 1---247 |  |  | A9TYBE640 |  | Acti9 iC40 | Acti9 iC40 |  |  |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | ARC iC40 | 1---247 |  |  | A9TAB2625 |  | Acti9 iC40 | Acti9 iC40 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | ARC iC40 | 1---247 |  |  | A9TAB2640 |  | Acti9 iC40 | Acti9 iC40 |  |  |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDEC606 |  |  |  | iCV40 ARC |  | 6A | 6A | 6A | 6A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDEC610 |  |  |  | iCV40 ARC |  | 10A | 10A | 10A | 10A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDEC613 |  |  |  | iCV40 ARC |  | 13A | 13A | 13A | 13A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDEC616 |  |  |  | iCV40 ARC |  | 16A | 16A | 16A | 16A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDEC620 |  |  |  | iCV40 ARC |  | 20A | 20A | 20A | 20A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDEC625 |  |  |  | iCV40 ARC |  | 25A | 25A | 25A | 25A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFC606 |  |  |  | iCV40 ARC |  | 6A | 6A | 6A | 6A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFC610 |  |  |  | iCV40 ARC |  | 10A | 10A | 10A | 10A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFC613 |  |  |  | iCV40 ARC |  | 13A | 13A | 13A | 13A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFC616 |  |  |  | iCV40 ARC |  | 16A | 16A | 16A | 16A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFC620 |  |  |  | iCV40 ARC |  | 20A | 20A | 20A | 20A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFC625 |  |  |  | iCV40 ARC |  | 25A | 25A | 25A | 25A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFC632 |  |  |  | iCV40 ARC |  | 32A | 32A | 32A | 32A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFC640 |  |  |  | iCV40 ARC |  | 40A | 40A | 40A | 40A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFD606 |  |  |  | iCV40 ARC |  | 6A | 6A | 6A | 6A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFD610 |  |  |  | iCV40 ARC |  | 10A | 10A | 10A | 10A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFD613 |  |  |  | iCV40 ARC |  | 13A | 13A | 13A | 13A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFD616 |  |  |  | iCV40 ARC |  | 16A | 16A | 16A | 16A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFD620 |  |  |  | iCV40 ARC |  | 20A | 20A | 20A | 20A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFD625 |  |  |  | iCV40 ARC |  | 25A | 25A | 25A | 25A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iCV40 ARC | 1---247 |  |  | A9TDFD632 |  |  |  | iCV40 ARC |  | 32A | 32A | 32A | 32A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPDD606 |  |  |  | iC40 ARC |  | 6A | 6A | 6A | 6A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPDD610 |  |  |  | iC40 ARC |  | 10A | 10A | 10A | 10A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPDD613 |  |  |  | iC40 ARC |  | 13A | 13A | 13A | 13A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPDD616 |  |  |  | iC40 ARC |  | 16A | 16A | 16A | 16A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPDD620 |  |  |  | iC40 ARC |  | 20A | 20A | 20A | 20A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPDD625 |  |  |  | iC40 ARC |  | 25A | 25A | 25A | 25A |  | Electricity | NA |  |  |  | NA | B | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPED606 |  |  |  | iC40 ARC |  | 6A | 6A | 6A | 6A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPED610 |  |  |  | iC40 ARC |  | 10A | 10A | 10A | 10A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPED613 |  |  |  | iC40 ARC |  | 13A | 13A | 13A | 13A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPED616 |  |  |  | iC40 ARC |  | 16A | 16A | 16A | 16A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | Frozen / Cancel | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPED620 |  |  |  | iC40 ARC |  | 20A | 20A | 20A | 20A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPED625 |  |  |  | iC40 ARC |  | 25A | 25A | 25A | 25A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPED632 |  |  |  | iC40 ARC |  | 32A | 32A | 32A | 32A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | iC40 ARC | 1---247 |  |  | A9TPED640 |  |  |  | iC40 ARC |  | 40A | 40A | 40A | 40A |  | Electricity | NA |  |  |  | NA | C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | VigiARC iC60 | 1---247 |  |  | A9TYBE225 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 1-2 1-3 2-1 2-3 3-1 3-2 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | VigiARC iC60 | 1---247 |  |  | A9TYBE240 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 1-2 1-3 2-1 2-3 3-1 3-2 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | VigiARC iC60 | 1---247 |  |  | A9TYAE225 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 1-2 1-3 2-1 2-3 3-1 3-2 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | VigiARC iC60 | 1---247 |  |  | A9TYAE240 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 1-2 1-3 2-1 2-3 3-1 3-2 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | ARC iC60 | 1---247 |  |  | A9TAB2225 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 1-2 1-3 2-1 2-3 3-1 3-2 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | ARC iC60 | 1---247 |  |  | A9TAB2240 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 1-2 1-3 2-1 2-3 3-1 3-2 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | ARC iC60 | 1---247 |  |  | A9TAA2225 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 1-2 1-3 2-1 2-3 3-1 3-2 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | ARC iC60 | 1---247 |  |  | A9TAA2240 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 1-2 1-3 2-1 2-3 3-1 3-2 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | VigiARC iDT40 | 1---247 |  |  | A9TYAE625 |  | Acti9 iDT40 | Acti9 iDT40 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | VigiARC iDT40 | 1---247 |  |  | A9TYAE640 |  | Acti9 iDT40 | Acti9 iDT40 |  |  |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | ARC iDT40 | 1---247 |  |  | A9TAA2625 |  | Acti9 iDT40 | Acti9 iDT40 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Active (Quattro) | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | ARC iDT40 | 1---247 |  |  | A9TAA2640 |  | Acti9 iDT40 | Acti9 iDT40 |  |  |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | 2A 4A 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Smart RCD | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | Vigi iDT40 | 1---247 |  |  | A9Y6E625 |  | Acti9 iDT40 | Acti9 iDT40 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Smart RCD | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | Vigi iDT40 | 1---247 |  |  | A9Y6E640 |  | Acti9 iDT40 | Acti9 iDT40 |  |  |  | 6A 10A 13A 16A 20A 25A 32A 40A |  | 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Smart RCD | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | Vigi iC40 | 1---247 |  |  | A9Y8E625 |  | Acti9 iC40 | Acti9 iC40 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Smart RCD | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | Vigi iC40 | 1---247 |  |  | A9Y8E640 |  | Acti9 iC40 | Acti9 iC40 |  |  |  | 6A 10A 13A 16A 20A 25A 32A 40A |  | 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 1P+N | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Smart RCD | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | Vigi iC60 | 1---247 |  |  | A9V6E225 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Smart RCD | Circuit Breaker | CIB + Mission Critical + SwoF IEC | Zigbee GP | Acti9 | Vigi iC60 | 1---247 |  |  | A9V6E240 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 6A 10A 13A 16A 20A 25A 32A 40A |  | 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Smart RCD | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | Vigi iC60 | 1---247 |  |  | A9V8E225 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 6A 10A 13A 16A 20A 25A |  | 6A 10A 13A 16A 20A 25A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / A9 Smart RCD | Circuit Breaker | CIB + Mission Critical | Zigbee GP | Acti9 | Vigi iC60 | 1---247 |  |  | A9V8E240 |  | Acti9 iC60 | Acti9 iC60 |  |  |  | 6A 10A 13A 16A 20A 25A 32A 40A |  | 6A 10A 13A 16A 20A 25A 32A 40A |  | Electricity | NA |  |  |  | NA | B C | NA | 2P | NA | NA | NA | NA | NA | NA | 1 2 3 | NA | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Control Device / PowerTag | I/O Device | CIB + Mission Critical | Zigbee Pro | PowerTag | C IO 230V | NA |  |  | A9XMC1D3 |  |  | tbd |  |  | NA | NA | NA | NA |  | No Commodity | No Commodity |  |  |  | NA | B C D | NA | 1P 1P+N 2P 3P 3P+N 4P | NA | NA | NA | NA | NA | NA | NA | NA | Direct / Line Reverse / Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / PowerTag | I/O Device | CIB + Mission Critical | Zigbee Pro | PowerTag | C 2DI 230V | NA |  |  | A9XMC2D3 |  |  | Acti 9 Vigi iC60 Acti 9 iCV40 Acti 9 Vigi iDPN Acti 9 Vigi DT40 Acti 9 Vigi C40 Acti 9 Vigi iC40 Acti 9 Vigi N40 Acti 9 iDD40 XA Acti 9 iCV40 XA Acti 9 Vigi iDT40 Acti 9 iDD40 Acti 9 Vigi iTG40 Acti 9 Vigi iCG40 None |  |  | NA | NA |  | 1A 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | No Commodity | No Commodity |  |  |  | NA | B C D | NA | 1P 1P+N 2P 3P 3P+N 4P | NA | NA | NA | NA | Signal Element List | NA | NA | NA | Direct / Line Reverse / Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Power Meter / PowerTag / NSX |  |  |  | PowerTag NSX | [28 empty] | NA
Power Meter / PowerTag / NSX | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | NSX 3P 250A | 1---247 |  |  | LV434020 |  |  | Compact NSX Compact NS TeSys GV5 TeSys GV7 |  |  | Min: 2A Max: 250A Step: 1A Default Value: 250A | NA |  | 100A 160A 250A to be completed with Tesys Values |  | Electricity | NA |  |  |  | B F N H S L R HB1 HB2 | TM-D TM-G MA µlogic 1.3M µlogic 2 µlogic Vigi4 µlogic 5 µlogic 6 µlogic Vigi7 | NA | 3P | NA | NA | NA | A | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Bottom Top | Top Bottom | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | SWAPB | no
Power Meter / PowerTag / NSX | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | NSX 3P 630A | 1---247 |  |  | LV434022 |  |  | Compact NSX Compact INV Compact INS Compact NS TeSys GV6 |  |  | Min: 5A Max: 630A Step: 1A Default Value: 630A | NA |  | 320A 400A 500A 630A to be completed with Tesys Values |  | Electricity | NA |  |  |  | B F N H S L R HB1 HB2 | TM-D TM-G MA µlogic 1.3M µlogic 2 µlogic Vigi4 µlogic 5 µlogic 6 µlogic Vigi7 | NA | 3P | NA | NA | NA | A | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Bottom Top | Top Bottom | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | SWAPB | no
Power Meter / PowerTag / NSX | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | NSX 3P+N 250A | 1---247 |  |  | LV434021 |  |  | Compact NSX Compact INV Compact INS Compact NS |  |  | Min: 2A Max: 250A Step: 1A Default Value: 250A | NA |  | 100A 125A 160A 200A 250A |  | Electricity | NA |  |  |  | B F N H S L R HB1 HB2 | TM-D TM-G MA µlogic 1.3M µlogic 2 µlogic Vigi4 µlogic 5 µlogic 6 µlogic Vigi7 | NA | 3P+N | NA | NA | NA | A | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Bottom Top | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | SWAPB | yes
Power Meter / PowerTag / NSX | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | NSX 3P+N 630A | 1---247 |  |  | LV434023 |  |  | Compact NSX Compact INV Compact INS Compact NS |  |  | Min: 5A Max: 630A Step: 1A Default Value: 630A | NA |  | 320A 400A 500A 630A |  | Electricity | NA |  |  |  | B F N H S L R HB1 HB2 | TM-D TM-G MA µlogic 1.3M µlogic 2 µlogic Vigi4 µlogic 5 µlogic 6 µlogic Vigi7 | NA | 3P+N | NA | NA | NA | A | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Bottom Top | Top Bottom | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | SWAPB | yes
Protection Device / Wireless OF-SD | I/O Device | CIB + Mission Critical | Zigbee GP |  | wireless auxiliary contact for Compact NSX | NA |  |  | LV429454 |  |  | Compact NSX Compact INV Compact INS Compact NS Powerpact H Powerpact J Powerpact L Easypact CVS Powerpact M Powerpact P Powerpact R |  |  | NA | NA |  | 100A 150A 160A 250A 400A 600A 630A 1200A |  | No Commodity | NA | [5 empty] | NA |  | NA | NA | NA |  | NA | YES NO (postponed) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Protection Device / Wireless OF-SD | I/O Device | CIB + Mission Critical | Zigbee GP |  | wireless auxiliary contact for Compact NSXm | NA |  |  | LV429453 |  |  | Compact NSXm Powerpact B |  |  | NA | NA |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A 70A 80A 90A 100A 110A 125A 160A |  | No Commodity | NA | [5 empty] | NA |  | NA | NA | NA |  | NA | YES NO (postponed) | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Power Meter / PowerTag / Rope |  |  |  | PowerTags Rope
Power Meter / PowerTag / Rope | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | R200 3P+N (IEC) | 1---247 |  |  | A9MEM1590 |  | NA | NA |  |  | Min: 2A Max: 200A Step: 1A Default Value: 200A | NA | NA | NA |  | Electricity | NA | [5 empty] | NA | 3P | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 1 2 3 | Top Bottom | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / Rope | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | R600 3P+N (IEC) | 1---247 |  |  | A9MEM1591 |  | NA | NA |  |  | Min: 5A Max: 600A Step: 1A Default Value: 600A | NA | NA | NA |  | Electricity | NA | [5 empty] | NA | 3P | NA | NA | NA | NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 1 2 3 | Top Bottom | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / Rope | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | R1000 3P+N (IEC) | 1---247 |  |  | A9MEM1592 |  | NA | NA |  |  | Min: 8A Max: 1000A Step: 1A Default Value: 1000A | NA | NA | NA |  | Electricity | NA | [5 empty] | NA | 3P | NA | NA | NA | A B | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 1 2 3 | Top Bottom | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / Rope | Power Meter
Power Meter / PowerTag / Rope | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | R2000 3P+N (IEC) | 1---247 |  |  | A9MEM1593 |  | NA | NA |  |  | Min: 15A Max: 2000A Step: 1A Default Value: 2000A | NA | NA | NA |  | Electricity | NA | [5 empty] | NA | 3P | NA | NA | NA | A B | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 1 2 3 | Top Bottom | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / Rope | Power Meter
Power Meter / PowerLogicTag / Rope | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | R120 3P+N (NEMA) | 1---247 |  |  | PLTR1203P |  | NA | NA |  |  | Min: 2A Max: 120A Step: 1A Default Value: 120A | NA | NA | NA |  | Electricity | NA | [5 empty] | NA | 3P | NA | NA | NA | NA | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A A B C | Line Load | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Rope | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | R600 3P+N (NEMA) | 1---247 |  |  | PLTR6003P |  | NA | NA |  |  | Min: 10A Max: 600A Step: 1A Default Value: 600A | NA | NA | NA |  | Electricity | NA | [5 empty] | NA | 3P | NA | NA | NA | A | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A A B C | Line Load | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Rope | Power Meter
Power Meter / PowerLogicTag / Rope | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | R1000 3P+N (NEMA) | 1---247 |  |  | PLTR10003P |  | NA | NA |  |  | Min: 15A Max: 1000A Step: 1A Default Value: 1000A | NA | NA | NA |  | Electricity | NA | [5 empty] | NA | 3P | NA | NA | NA | A B | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A A B C | Line Load | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Rope | Power Meter
Power Meter / PowerLogicTag / Rope | Power Meter
Power Meter / PowerLogicTag / Rope | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | R2000 3P+N (NEMA) | 1---247 |  |  | PLTR20003P |  | NA | NA |  |  | Min: 30A Max: 2000A Step: 1A Default Value: 2000A | NA | NA | NA |  | Electricity | NA | [5 empty] | NA | 3P | NA | NA | NA | A B | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A A B C | Line Load | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Rope | Power Meter
Power Meter / PowerLogicTag / Rope | Power Meter
Power Meter / PowerTag / HR |  |  |  | PowerTag 160A
Power Meter / PowerTag / HR | Power Meter | CIB + Mission Critical + SwoF IEC | Zigbee GP | PowerTag | F160 3P+N (IEC) | 1---247 |  |  | A9MEM1580 |  |  | Acti 9 C120 Acti 9 NG125 ComPact NSXm TeSys GV4 Compact INS Acti 9 iSW Acti 9 iSW-NA Acti 9 iID PowerPact B |  |  | Min: 2A Max: 160A Step: 1A Default Value: 160A | NA |  | 16A 20A 25A 32A 40A 50A 63A 80A 100A 125A 160A |  | Electricity | NA |  |  |  | E B F N H | TM-D µlogic Vigi4.1 B C D | NA | 3P 3P+N | NA | NA | NA | A NA | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | Top Bottom | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerTag / HR | Power Meter
Power Meter / PowerTag / HR | Power Meter
Power Meter / PowerTag / HR | Power Meter
Power Meter / PowerTag / HR | Power Meter
Power Meter / PowerTag / HR | Power Meter
Power Meter / PowerTag / HR | Power Meter
Power Meter / PowerTag / HR | Power Meter
Power Meter / PowerLogicTag / HR | Power Meter | CIB + Mission Critical | Zigbee GP | PowerLogicTag | F160 3P+N (NEMA) | 1---247 |  |  | PLTPPB1253P |  | PowerPact B | PowerPact B |  |  |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A 70A 80A 90A 100A 110A 125A |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A 70A 80A 90A 100A 110A 125A |  | Electricity | NA |  |  |  |  | T-M | NA | 3P 3P+N | NA | NA | NA | A | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | Line Load | Direct Reverse | 3PH4W 3PH3W | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag / HR | Power Meter
Power Meter / PowerLogicTag / Q0 |  |  |  | PowerTags Square D QO
Power Meter / PowerLogicTag / Q0 | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 1P+ N 120V QO 10-30 | 1---247 |  |  | PLTQO301P |  | QO | QO |  |  |  | 10A 15A 20A 25A 30A |  | 10A 15A 20A 25A 30A |  | Electricity | NA |  |  |  | NA | NA | NA | 1P+N | NA | NA | NA | NA | NA | YES NO | A B C | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Q0 | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 1P+ N 120V QO 35-60 | 1---247 |  |  | PLTQO601P |  | QO | QO |  |  |  | 35A 40A 45A 50A 60A |  | 35A 40A 45A 50A 60A |  | Electricity | NA |  |  |  | NA | NA | NA | 1P+N | NA | NA | NA | NA | NA | YES NO | A B C | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Q0 | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 2P 208-240V QO 10-30 | 1---247 |  |  | PLTQO302P |  | QO | QO |  |  |  | 10A 15A 20A 25A 30A |  | 10A 15A 20A 25A 30A |  | Electricity | NA |  |  |  | NA | NA | NA | 2P | NA | NA | NA | NA | NA | YES NO | A-B B-A A-C C-A B-C C-B | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Q0 | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 2P 208-240 QO 35-60 | 1---247 |  |  | PLTQO602P |  | QO | QO |  |  |  | 35A 40A 45A 50A 60A |  | 35A 40A 45A 50A 60A |  | Electricity | NA |  |  |  | NA | NA | NA | 2P | NA | NA | NA | NA | NA | YES NO | A-B B-A A-C C-A B-C C-B | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Q0 | Power Meter | Not supported by iOT Bridge | Zigbee GP | PowerLogicTag | 2P 208-240 QO 70-125 | 1---247 |  |  | PLTQO1252P |  | QO | QO |  |  |  | 70A 80A 90A 100A 110A 125A |  | 70A 80A 90A 100A 110A 125A |  | Electricity | NA |  |  |  | NA | NA | NA | 2P | NA | NA | NA | NA | NA | YES NO | A-B B-A A-C C-A B-C C-B | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag / Q0 | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 3P 208-240 QO 10-30 | 1---247 |  |  | PLTQO303P |  | QO | QO |  |  |  | 10A 15A 20A 25A 30A |  | 10A 15A 20A 25A 30A |  | Electricity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Q0 | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 3P 208-240 QO 35-60 | 1---247 |  |  | PLTQO603P |  | QO | QO |  |  |  | 35A 40A 45A 50A 60A |  | 35A 40A 45A 50A 60A |  | Electricity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / Q0 | Power Meter | Not supported by iOT Bridge | Zigbee GP | PowerLogicTag | 3P 208-240 QO 70-125 | 1---247 |  |  | PTQO1253P |  | QO | QO |  |  |  | 70A 80A 90A 100A 110A 125A |  | 70A 80A 90A 100A 110A 125A |  | Electricity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag |  |  |  | PowerTags Square D Q&B | [32 empty] | Top / Line Bottom / Load
Power Meter / PowerLogicTag | Power Meter | Not supported by iOT Bridge | Zigbee GP | PowerLogicTag | PP-Q/B 125 2P | 1---247 |  |  | PLTPP1252P |  |  | PowerPact Q Frame PowerPact B Frame |  |  | 125A | 125A | 125A | 125A |  | Electricity | NA |  |  |  |  | T-M | NA | 2P | NA | NA | NA | A | NA | YES NO | A-B B-A A-C C-A B-C C-B | Bottom / Load | Top / Line Bottom / Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag | Power Meter | Not supported by iOT Bridge | Zigbee GP | PowerLogicTag | PP-Q/B 125 3P | 1---247 |  |  | PLTPP1253P |  |  | PowerPact Q Frame PowerPact B Frame |  |  | 125A | 125A | 125A | 125A |  | Electricity | NA |  |  |  |  | T-M | NA | 3P | NA | NA | NA | A | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | Bottom / Load | Top / Line Bottom / Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag / E-Frame |  |  |  | PowerTags Square D E-Frame
Power Meter / PowerLogicTag / E-Frame | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 1P+ N 277V EDB 10-60 | 1---247 |  |  | PLTE601P |  | E Frame | E Frame |  |  |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A |  | Electricity | NA |  |  |  | NA | NA | NA | 1P+N | NA | NA | NA | NA | NA | YES NO | A B C | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / E-Frame | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 2P 480V EDB 10-60 | 1---247 |  |  | PLTE602P |  | E Frame | E Frame |  |  |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A |  | Electricity | NA |  |  |  | NA | NA | NA | 2P | NA | NA | NA | NA | NA | YES NO | A-B B-A A-C C-A B-C C-B | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / E-Frame | Power Meter | Frozen / Cancel | Zigbee GP | PowerLogicTag | 2P 480V EDB 70-125 | 1---247 |  |  |  |  | E Frame | E Frame |  |  |  | 70A 80A 90A 100A 110A 125A |  | 70A 80A 90A 100A 110A 125A |  | Electricity | NA |  |  |  | NA | NA | NA | 2P | NA | NA | NA | NA | NA | YES NO | A-B B-A A-C C-A B-C C-B | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag / E-Frame | Power Meter | CIB + Mission Critical + NEC2020 + SwoF NEMA | Zigbee GP | PowerLogicTag | 3P 480V EDB 10-60 | 1---247 |  |  | PLTE603P |  | E Frame | E Frame |  |  |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A |  | 15A 20A 25A 30A 35A 40A 45A 50A 60A |  | Electricity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES |  |  | DIRECT | no
Power Meter / PowerLogicTag / E-Frame | Power Meter | Frozen / Cancel | Zigbee GP | PowerLogicTag | 3P 480V EDB 70-125 | 1---247 |  |  |  |  | E Frame | E Frame |  |  |  | 70A 80A 90A 100A 110A 125A |  | 70A 80A 90A 100A 110A 125A |  | Electricity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | Load | Line Load | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag |  |  |  | PowerTags Square D H,J,L Frame |  | 1---247
Power Meter / PowerLogicTag | Power Meter | Frozen / Cancel | Zigbee GP | PowerLogicTag | PP-H 150 3P | 1---247 |  |  | PLTPPH1503P |  | PowerPact H Frame | PowerPact H Frame |  |  | 150A | 150A | 150A | 150A |  | Electricity | NA |  |  |  | D G J L | T-M M µlogic 1.3M µlogic 2 µlogic 3 µlogic 3S µlogic 5 µlogic 6 | NA | 3P | NA | NA | NA | A | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag | Power Meter | Frozen / Cancel | Zigbee GP | PowerLogicTag | PP-J 250 3P | 1---247 |  |  | PLTPPJ2503P |  | PowerPact J Frame | PowerPact J Frame |  |  | 250A | 250A | 250A | 250A |  | Electricity | NA |  |  |  | D G J L | T-M M µlogic 1.3M µlogic 2 µlogic 3 µlogic 3S µlogic 5 µlogic 6 | NA | 3P | NA | NA | NA | A | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Power Meter / PowerLogicTag | Power Meter | Frozen / Cancel | Zigbee GP | PowerLogicTag | PP-L 600 3P | 1---247 |  |  | PLTPPL6003P |  | PowerPact L Frame | PowerPact L Frame |  |  | 600A | 600A | 600A | 600A |  | Electricity | NA |  |  |  | D G J L | T-M M µlogic 1.3M µlogic 2 µlogic 3 µlogic 3S µlogic 5 µlogic 6 | NA | 3P | NA | NA | NA | A | NA | YES NO | A-B-C A-C-B B-C-A B-A-C C-A-B C-B-A | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Sensor | Ambient sensor | CIB + Mission Critical | Zigbee GP | Easergy | TH110 | NA |  |  | EMS59440 |  |  | Equipment Type List |  |  | NA | NA | NA | NA |  | Environment | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Sensor Position List | Measured Point List | Cubicle ID | Cubicle Type | Circuit Breaker ID | NA |  |  |  |  | NA | NA | NA | Usage List | NA |  | Through PaS | YES | YES
Sensor | Ambient sensor | CIB + Mission Critical | Zigbee GP | Easergy | CL110 | NA |  |  | EMS59443 |  |  | Equipment Type List |  |  | NA | NA | NA | NA |  | Environment | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Sensor Position List | Measured Point List | Cubicle ID | Cubicle Type | NA | Drawer ID |  |  |  |  | NA | NA | NA | Usage List | NA |  | Through PaS | YES | YES
Sensor | Ambient sensor | CIB + Mission Critical | Zigbee GP | Easergy | CT110 | NA | [5 empty] | NA |  |  | NA | NA | NA | NA |  | Environment | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | ? | ?
Sensor | Ambient sensor | CIB + Mission Critical | Zigbee GP | Easergy | OZ110 | NA | [5 empty] | NA |  |  | NA | NA | NA | NA |  | Environment | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | ? | ?
Sensor | Ambient sensor | CIB + Mission Critical | Zigbee GP | PowerTag | PowerTag A | NA |  |  | A9XST114 |  |  | NA |  |  | NA | NA | NA | NA |  | Environment | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | ? | ?
Sensor | Ambient sensor | CIB + Mission Critical | Zigbee GP | EwSense | EwSenseTemp | NA |  |  | A9XST114 |  |  | NA |  |  | NA | NA | NA | NA |  | Environment | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  | Usage List |  |  |  | Usage List | NA |  | Through PaS
Sensor | Ambient sensor | CIB + Mission Critical | Zigbee Pro | E-Sensor | CO2 TRH | NA |  |  | SED-CO2-G5045 |  |  | NA |  |  | NA | NA | NA | NA |  | Environment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | ? | ?
Sensor | Ambient sensor | CIB + Mission Critical | Zigbee Pro | E Sensor | TRH | NA |  |  | SED-TRH-G-5045 |  |  | NA |  |  | NA | NA | NA | NA |  | Environment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | ? | ?
Sensor | Ambient sensor | CIB + Mission Critical + SwoF IEC | Zigbee Pro | Heat Tag | HeatTag cable overheating sensor IEC | NA |  |  | SMT10020/A9N18543 |  |  | Equipment Type List |  |  | NA | NA | NA | NA |  | Environment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Sensor Position List | Measured Point List | Cubicle ID | Cubicle Type | NA | Drawer ID |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Sensor | Ambient sensor | CIB + Mission Critical + SwoF NEMA | Zigbee Pro | Heat Tag | HeatTag cable overheating sensor NEMA | NA | [5 empty] | Equipment Type List |  |  | NA | NA | NA | NA |  | Environment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Sensor Position List | Measured Point List | Cubicle ID | Cubicle Type | NA | Drawer ID | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Sensor | Ambient sensor | CIB + Mission Critical | Lora | Heat Tag | HeatTag cable overheating sensor Lora | NA | [5 empty] | Equipment Type List |  |  | NA | NA | NA | NA |  | Environment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Sensor Position List | Measured Point List | Cubicle ID | Cubicle Type | NA | Drawer ID |  |  |  |  | NA | NA | NA | NA | NA |  | ? | ? | ?
Sensor | Ambient sensor | CIB + Mission Critical | Sigfox | Heat Tag | HeatTag cable overheating sensor Sigfox | NA | [5 empty] | Equipment Type List |  |  | NA | NA | NA | NA |  | Environment | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Sensor Position List | Measured Point List | Cubicle ID | Cubicle Type | NA | Drawer ID |  |  |  |  | NA | NA | NA | NA | NA |  | ? | ? | ?
Gateway | I/O Device | CIB + Mission Critical | Modbus SL | Acti9 | SmartLink (aka Legacy) |  | NA |  | A9XMSB11 |  | Acti9 | Acti9 | SmartLink (aka Legacy) |  | NA | NA | NA | NA |  | No Commodity | NA |  | A9XMSB11 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Gateway | I/O Device | CIB + Mission Critical | Modbus SL | Acti9 | SmartLink (aka Refresh Modbus) |  | NA |  | SL-MOD-PLUS |  | Acti9 | Acti9 | SmartLink (aka Refresh Modbus) |  | NA | NA | NA | NA |  | No Commodity | NA |  | SL-MOD-PLUS |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Gateway | I/O Device | CIB + Mission Critical | Modbus SL + Zigbee | Acti9 | SmartLink (aka Refresh Modbus + Zigbee) |  | NA |  | SL-MOD-ZB |  | Acti9 | Acti9 | SmartLink (aka Refresh Modbus + Zigbee) |  | NA | NA | NA | NA |  | No Commodity | NA |  | SL-MOD-ZB |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Gateway | Gateway & Server | Mission Critical | Modbus SL | Harmony XBR5 | ZBRN32 (aka 'Sologate') |  | NA |  | ZBRN32 |  | Harmony XBR5 | Harmony XBR5 | ZBRN32 (aka 'Sologate') |  | NA | NA | NA | NA |  | No Commodity | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | PowerLogic | EGX100 | NA | NA |  | EGX100 |  | PowerLogic | PowerLogic | EGX100 |  | NA | NA | NA | NA |  | No Commodity | NA |  | EGX100 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | PowerLogic | EGX300 | NA | NA |  | EGX300 |  | PowerLogic | PowerLogic | EGX300 |  | NA | NA | NA | NA |  | No Commodity | NA |  | EGX300 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Enerlin'X | Link150 | NA | NA |  | EGX150 |  | Enerlin'X | Enerlin'X | Link150 |  | NA | NA | NA | NA |  | No Commodity | NA |  | EGX150 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Acti9 | PowerTag Link | NA | NA |  | A9XMWA20 |  | Acti9 | Acti9 | PowerTag Link |  | NA | NA | NA | NA |  | No Commodity | NA |  | A9XMWA20 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | PowerLogic | Com'X200 | NA | NA |  | EBX200 |  | PowerLogic | PowerLogic | Com'X200 |  | NA | NA | NA | NA |  | No Commodity | NA |  | EBX200 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | PowerLogic | Com'X210 | NA | NA |  | EBX210 |  | PowerLogic | PowerLogic | Com'X210 |  | NA | NA | NA | NA |  | No Commodity | NA |  | EBX210 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | PowerLogic | Com'X510 | NA | NA |  | EBX510 |  | PowerLogic | PowerLogic | Com'X510 |  | NA | NA | NA | NA |  | No Commodity | NA |  | EBX510 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | YES (Partial)
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Ecostruxure Panel Server | PAS600 (BPaS) | NA | NA |  | PAS600 |  | Ecostruxure Panel Server | Ecostruxure Panel Server | PAS600 (BPaS) |  | NA | NA | NA | NA |  | No Commodity | NA |  | PAS600 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | YES
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Ecostruxure Panel Server | PAS600L (BPaS) | NA | NA |  | PAS600L |  | Ecostruxure Panel Server | Ecostruxure Panel Server | PAS600L (BPaS) |  | NA | NA | NA | NA |  | No Commodity | NA |  | PAS600L |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | YES
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Ecostruxure Panel Server | PAS600T (BPaS) | NA | NA |  | PAS600T |  | Ecostruxure Panel Server | Ecostruxure Panel Server | PAS600T (BPaS) |  | NA | NA | NA | NA |  | No Commodity | NA |  | PAS600T |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | YES
Gateway | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Ecostruxure Panel Server | PAS800L (APaS) | NA | NA |  | PAS600L |  | Ecostruxure Panel Server | Ecostruxure Panel Server | PAS800L (APaS) |  | NA | NA | NA | NA |  | No Commodity | NA |  | PAS600L |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | YES
Gateway / DI Status | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Ecostruxure Panel Server | PAS600L (BPaS) | NA | NA |  | PAS600L |  | ? | ? |  |  | NA | NA | NA | NA |  | No Commodity | NA | ? | ? | ? | NA | NA | NA | NA | NA | NA | NA | NA | Signal Element List | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Gateway / DI Pulse Counter | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Ecostruxure Panel Server | PAS600L (BPaS) | NA | NA |  | PAS600L |  | ? | ? |  |  | NA | NA | NA | NA |  |  | Commodity List | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Gateway / DI Status | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Ecostruxure Panel Server | PAS800L (APaS) | NA | NA |  | PAS600L |  | ? | ? |  |  | NA | NA | NA | NA |  | No Commodity | NA | ? | ? | ? | NA | NA | NA | NA | NA | NA | NA | NA | Signal Element List | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Gateway / DI Pulse Counter | Gateway & Server | CIB + Mission Critical | Modbus/TCP | Ecostruxure Panel Server | PAS800L (APaS) | NA | NA |  | PAS600L |  | ? | ? |  |  | NA | NA | NA | NA |  |  | Commodity List | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel iOFSDt | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | Acti9 iOF+SD24 top connector | NA | NA |  | A9A26897 |  |  | Acti 9 iC60 Acti 9 iDPN Vigi Acti 9 iID Acti 9 iSW-NA Acti 9 iC60 RCBO Acti 9 iC65 Acti 9 ARA Acti 9 RCA Acti 9 iDPN (China version) Acti 9 iC40 |  |  |  | 1A 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | 1A 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | No Commodity | NA |  | A9A26897 |  | NA | B C D | NA | 1P 1P+N 2P 3P 3P+N 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel iOFSDb | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | Acti9 iOF+SD24 bottom connector | NA | NA |  | A9A26898 |  |  | Acti 9 iC60 Acti 9 iDPN Vigi Acti 9 iID Acti 9 iSW-NA Acti 9 iC60 RCBO Acti 9 iC65 Acti 9 ARA Acti 9 RCA Acti 9 iDPN (China version) Acti 9 iC40 |  |  |  | 1A, 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | 1A, 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | No Commodity | NA |  | A9A26898 |  | NA | B C D | NA | 1P 1P+N 2P 3P 3P+N 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / SmartLink /Chanel RCA | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | Acti9 RCAiC60 | NA | NA |  | A9C70122 |  |  | IC60 2P IC60 1P + N IC60 1P IC65 1P IC65 2P |  |  |  | 1A, 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | 1A, 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | No Commodity | NA |  | A9C70122 |  | NA | B C D | NA | 1P 1P+N 2P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel Reflex | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | Acti9 Reflex iC60 | NA | NA |  | A9C6xxxx |  | Acti9 Reflex iC60 | Acti9 Reflex iC60 |  |  |  | 1A, 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | 1A, 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | No Commodity | NA |  | A9C6xxxx |  | NA | B C D | NA | 2P 3P 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel iATL | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | ActI9 iATL24 | NA | NA |  | A9C15424 |  |  |  | ActI9 iATL24 |  | NA | NA | NA | NA |  | No Commodity | NA |  | A9C15424 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel iACT | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | Acti9 iACT24 | NA | NA |  | A9C15924 |  |  |  | Acti9 iACT24 |  | NA | NA | NA | NA |  | No Commodity | NA |  | A9C15924 |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel OF | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | Acti9 OF24 | NA | NA |  | A9N26898 |  |  | Acti 9 Vigi iC60 Acti 9 iCV40 Acti 9 Vigi iDPN Acti 9 Vigi DT40 Acti 9 Vigi C40 Acti 9 Vigi iC40 Acti 9 Vigi N40 Acti 9 iDD40 XA Acti 9 iCV40 XA Acti 9 Vigi iDT40 Acti 9 iDD40 Acti 9 Vigi iTG40 Acti 9 Vigi iCG40 None |  |  |  | 1A 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | 1A 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | No Commodity | NA |  | A9N26898 |  | NA | B C D | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel SD | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | ActI9 SD24 | NA | NA |  | A9N26898 |  |  | Acti 9 Vigi iC60 Acti 9 iCV40 Acti 9 Vigi iDPN Acti 9 Vigi DT40 Acti 9 Vigi C40 Acti 9 Vigi iC40 Acti 9 Vigi N40 Acti 9 iDD40 XA Acti 9 iCV40 XA Acti 9 Vigi iDT40 Acti 9 iDD40 Acti 9 Vigi iTG40 Acti 9 Vigi iCG40 None |  |  |  | 1A 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | 1A 1,6A 2A 3A 4A 5A 6A 10A 16A 20A 25A 32A 40A 50A 63A |  | No Commodity | NA |  | A9N26898 |  | NA | B C D | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel Counter | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | Counter | NA | NA | NA | NA |  | ? | ? |  |  | NA | NA | NA | NA |  |  | Commodity List |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Control Device / SmartLink / Chanel Standard IO | I/O Device | CIB + Mission Critical | Modbus SL via SmartLink | Acti9 | Standard IO | NA | NA | NA | NA |  | ? | ? |  |  | NA | NA | NA | NA |  | No Commodity | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | Signal Element List | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | Compact NSX - µLogic NSX A (5.x,6.x, 7.x) |  | NA |  |  |  | Compact NSX | Compact NSX |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 100A 160A 250A 400A 630A |  |  | No Commodity | NA |  |  |  | B F N H S L R HB1 HB2 | µlogic 5 µlogic 6 µlogic Vigi7 | A | 3P 4P | NA | NA | NA | A | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | Compact NSX - µLogic NSX E (5.x,6.x, 7.x) |  | NA |  |  |  | Compact NSX | Compact NSX |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 100A 160A 250A 400A 630A |  |  | Electricity | NA |  |  |  | B F N H S L R HB1 HB2 | µlogic 5 µlogic 6 µlogic Vigi7 | E | 3P 4P | NA | NA | NA | A | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | PowerPactHJL - µLogic NSX A (5.x, 6.x) |  | NA |  |  |  |  | Powerpact H Frame Powerpact J Frame Powerpact L Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 150A 250A 400A 600A 1200A |  |  | No Commodity | NA |  |  |  | D G J L | µlogic 5 µlogic 6 | A | 3P 4P | NA | NA | NA | A | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | PowerPactHJL - µLogic NSX E (5.x, 6.x) |  | NA |  |  |  |  | Powerpact H Frame Powerpact J Frame Powerpact L Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 150A 250A 400A 600A 1200A |  |  | Electricity | NA |  |  |  | D G J L | µlogic 5 µlogic 6 | E | 3P 4P | NA | NA | NA | A | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | Mission Critical | Modbus SL | Micrologic | Compact NS/PowerPact MPR - µLogic A (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | A | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | Compact NS/PowerPact MPR - µLogic E (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | E | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | Compact NS/PowerPact MPR - µLogic P (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | P | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | Mission Critical | Modbus SL | Micrologic | Compact NS/PowerPact MPR - µLogic H (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | H | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | Mission Critical | Modbus SL | Micrologic | Masterpact NT/NW - µLogic A (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | A | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | Masterpact NT/NW - µLogic E (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | E | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | Masterpact NT/NW - µLogic P (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | P | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | Mission Critical | Modbus SL | Micrologic | Masterpact NT/NW - µLogic H (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | H | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus SL | Micrologic | Masterpact MTZ - µLogic X (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact MTZ1 Masterpact MTZ2 Masterpact MTZ3 |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | X | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | Compact NSX - µLogic NSX A (5.x,6.x, 7.x) |  | NA |  |  |  | Compact NSX | Compact NSX |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 100A 160A 250A 400A 630A |  |  | No Commodity | NA |  |  |  | B F N H S L R HB1 HB2 | µlogic 5 µlogic 6 µlogic Vigi7 | A | 3P 4P | NA | NA | NA | A | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | Compact NSX - µLogic NSX E (5.x,6.x, 7.x) |  | NA |  |  |  | Compact NSX | Compact NSX |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 100A 160A 250A 400A 630A |  |  | Electricity | NA |  |  |  | B F N H S L R HB1 HB2 | µlogic 5 µlogic 6 µlogic Vigi7 | E | 3P 4P | NA | NA | NA | A | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | PowerPactHJL - µLogic NSX A (5.x, 6.x) |  | NA |  |  |  |  | Powerpact H Frame Powerpact J Frame Powerpact L Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 150A 250A 400A 600A 1200A |  |  | No Commodity | NA |  |  |  | D G J L | µlogic 5 µlogic 6 | A | 3P 4P | NA | NA | NA | A | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | PowerPactHJL - µLogic NSX E (6.x, 7.x) |  | NA |  |  |  |  | Powerpact H Frame Powerpact J Frame Powerpact L Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 150A 250A 400A 600A 1200A |  |  | Electricity | NA |  |  |  | D G J L | µlogic 5 µlogic 6 | E | 3P 4P | NA | NA | NA | A | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | Mission Critical | Modbus/TCP | Micrologic | Compact NS/PowerPact MPR - µLogic A (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | A | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | Compact NS/PowerPact MPR - µLogic E (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | E | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | Compact NS/PowerPact MPR - µLogic P (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | P | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | Mission Critical | Modbus/TCP | Micrologic | Compact NS/PowerPact MPR - µLogic H (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | H | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | Mission Critical | Modbus/TCP | Micrologic | Masterpact NT/NW - µLogic A (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | A | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | Masterpact NT/NW - µLogic E (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | E | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | Masterpact NT/NW - µLogic P (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | P | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | Mission Critical | Modbus/TCP | Micrologic | Masterpact NT/NW - µLogic H (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | H | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | CIB + Mission Critical | Modbus/TCP | Micrologic | Masterpact MTZ - µLogic X (2.x, 3.x, 5.x, 6.x, 7.x) |  | NA |  |  |  |  | Masterpact MTZ1 Masterpact MTZ2 Masterpact MTZ3 |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | X | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Direct | YES | YES
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker / BCM Wireless | Circuit Breaker | CIB + Mission Critical + SwoF NEMA | Zigbee | Micrologic | Wireless Breaker Communication Module |  | NA |  | 33102 |  |  | Compact NS PowerPact M Frame PowerPact P Frame PowerPact R Frame |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 300A 350A 400A 450A 500A 600A 630A 700A 800A 1000A 1200A 1250A 1600A 2000A 2500A 3000A 3200A |  |  | Electricity | NA |  |  |  | N H L LB G J K L | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | P H | 2P 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker / BCM Wireless | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker / BCM Wireless | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker / BCM Wireless | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker / BCM Wireless | Circuit Breaker | CIB + Mission Critical + SwoF NEMA | Zigbee | Micrologic | Wireless Breaker Communication Module |  | NA |  | 33102 |  |  | Masterpact NT Masterpact NW |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA |  |  |  | N1 H1 H2 H3 L1 | µlogic 2.0 µlogic 3.0 µlogic 5.0 µlogic 6.0 µlogic 7.0 | P H | 3P 4P | NA | NA | NA | A B | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Breaker / BCM Wireless | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Breaker / PowerTag MTZ | Circuit Breaker | Mission Critical + SwoF NEMA | Zigbee GP | PowerTag | Protection Device / Breaker / PowerTag MTZ | NA | [5 empty] | Masterpact MTZ1 Masterpact MTZ2 Masterpact MTZ3 |  |  | Register reading |  | Register reading The return value shall be 1 of the values below: 250A 630A 800A 1000A 1250A 1600A 2000A 2500A 3200A 4000A 5000A 6300A |  |  | Electricity | NA | [7 empty] | NA | NA | NA |  | NA | YES NO | 1-2-3 1-3-2 2-3-1 2-1-3 3-1-2 3-2-1 | NA | NA |  | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | Load Type List |  | Through PaS | YES | YES
Protection Device / Switch Disconnector | Circuit Breaker | CIB + Mission Critical | Modbus SL | BSCM | BSCM with IFM (switch disconnector) |  | NA |  |  |  |  | Compact NSX NA switch disconnector Powerpact H Frame switch disconnector Powerpact J Frame switch disconnector Powerpact L Frame switch disconnector |  |  | NA | NA |  | 100A 150A 160A 250A 400A 600A 630A |  | No Commodity | NA |  |  |  | NA | NA | NA | 3P 4P | NA | NA | NA | NA | NA | YES NO | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [7 empty] | Usage List | NA |  | Through PaS | YES | YES
Protection Device / Switch Disconnector | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Switch Disconnector | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Protection Device / Switch Disconnector | Circuit Breaker | [35 empty] | NA | NA | NA | NA | NA | NA | NA | NA
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby) | Transferpact FX |  | NA |  | TA10D2LXXX3TPE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 50A 63A 80A 100A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 2P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby) | Transferpact FX |  | NA |  | TA10D3LXXX4TPE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 32A 40A 50A 63A 80A 100A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby) | Transferpact FX |  | NA |  | TA10D4LXXX4TPE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 32A 40A 50A 63A 80A 100A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby) | Transferpact FX |  | NA |  | TA16D3LXXX4TPE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 80A 100A 125A 160A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby) | Transferpact FX |  | NA |  | TA16D4LXXX4TPE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 80A 100A 125A 160A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby Plus) | Transferpact FX |  | NA |  | TA25D3LXXX2PE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 100A 200A 250A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby Plus) | Transferpact FX |  | NA |  | TA25D4LXXX2PE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 100A 200A 250A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby Plus) | Transferpact FX |  | NA |  | TA25D3LXXX4PE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 100A 200A 250A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby Plus) | Transferpact FX |  | NA |  | TA25D4LXXX4PE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 100A 200A 250A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby Plus) | Transferpact FX |  | NA |  | TA63D3LXXX2PE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 320A 400A 500A 630A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby Plus) | Transferpact FX |  | NA |  | TA63D4LXXX2PE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 320A 400A 500A 630A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby Plus) | Transferpact FX |  | NA |  | TA63D3LXXX4PE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 320A 400A 500A 630A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 3P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Transfer Switch | Transfer Switch | Mission Critical | Modbus SL | TransferPact (aka Ruby Plus) | Transferpact FX |  | NA |  | TA63D4LXXX4PE |  | Transferpact FX | Transferpact FX |  |  | NA | NA | Register reading The return value shall be 1 of the values below: 320A 400A 500A 630A |  | NA | No Commodity | NA |  |  |  | NA | NA | NA | 4P | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IM400 |  | NA |  | IMD-IM400 |  | Vigilohm | Vigilohm | IM400 |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IM400L |  | NA |  | IMDIM400L |  | Vigilohm | Vigilohm | IM400L |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IM400C |  | NA |  | IMD-IM400C |  | Vigilohm | Vigilohm | IM400C |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IM400THR |  | NA |  | IMDIM400THR |  | Vigilohm | Vigilohm | IM400THR |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IM400LTHR |  | NA |  | IMDIM400LTHR |  | Vigilohm | Vigilohm | IM400LTHR |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IM20 |  | NA |  | IMD-IM20 |  | Vigilohm | Vigilohm | IM20 |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IM20H |  | NA |  | IMD-IM20-H |  | Vigilohm | Vigilohm | IM20H |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IFL12C |  | NA |  | IMDIFL12C |  | Vigilohm | Vigilohm | IFL12C |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IFL12MC |  | NA |  | IMDIFL12MC |  | Vigilohm | Vigilohm | IFL12MC |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IFL12LMC |  | NA |  | IMDIFL12LMC |  | Vigilohm | Vigilohm | IFL12LMC |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IFL12MCT |  | NA |  | IMDIFL12MCT |  | Vigilohm | Vigilohm | IFL12MCT |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IFL12LMCT |  | NA |  | IMDIFL12LMCT |  | Vigilohm | Vigilohm | IFL12LMCT |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / Vigilohm | Insultation Ctrl | Mission Critical | Modbus SL | Vigilohm | IFL12H |  | NA |  | IMDIFL12H |  | Vigilohm | Vigilohm | IFL12H |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Cond. Monitoring | Cond. Monitoring | Mission Critical | Modbus/SL | Ecostruxure Operation Server | BM100 (aka BMM Breaker Monitoring Module) |  | NA |  | EATDIGBMMS | [5 empty] | NA | NA | NA | NA |  | No Commodity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Cond. Monitoring | Cond. Monitoring | Mission Critical | Modbus/SL | Ecostruxure Operation Server | PTM100 (aka GMM Gas Monitoring Module) |  | NA |  | EATDIGGMMS | [5 empty] | NA | NA | NA | NA |  | No Commodity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Cond. Monitoring | Cond. Monitoring | Mission Critical | Zigbee Pro | PowerLogic | PD100 (aka Partial Discharge Box Vivaldi) | NA |  |  | PD100X001 |  |  | Equipment Type List |  |  | NA | NA | NA | NA |  | No Commodity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | Cubicle ID | NA | Circuit Breaker ID | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Cond. Monitoring | Cond. Monitoring | Mission Critical | Zigbee Pro | Ecostruxure Operation Server | MCM100 (aka MCM) |  | NA |  | EATDIGMCMM1 | [5 empty] | NA | NA | NA | NA |  | No Commodity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Cond. Monitoring | Cond. Monitoring | Mission Critical | Zigbee Pro | Ecostruxure Operation Server | MCM200 (aka MCM) |  | NA |  | EATDIGMCMM2 | [5 empty] | NA | NA | NA | NA |  | No Commodity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | YES
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Easergy P3 | P3Uxx |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Easergy P3 | P3F30 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Easergy P3 | P3L30 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Easergy P3 | P3Uxx |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Easergy P3 | P3F30 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Easergy P3 | P3L30 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Easergy P5 | P5U20 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Easergy P5 | P5F30 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Easergy P5 | P5U20 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Easergy P5 | P5F30 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Easergy P7 |  |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | S80 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | S81 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | S82 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | S83 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | S84 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | T81 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | T82 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | T87 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | M81 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | M87 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | M88 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | G82 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | G87 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | G88 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | B80 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | B83 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus SL | Sepam Series 80 | C86 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | S80 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | S81 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | S82 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | S83 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | S84 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | T81 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | T82 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | T87 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | M81 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | M87 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | M88 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | G82 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | G87 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | G88 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | B80 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | B83 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Protection Device / MV Relay | Protection relay | Mission Critical | Modbus/TCP | Sepam Series 80 | C86 |  | NA | [12 empty] | Electricity | NA | [7 empty] | NA | NA | NA |  | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Control Device / PFC Controller / Varlogic | Power quality | Mission Critical | Modbus SL | VarPlus Logic | VL6 |  | NA |  | VPL06N |  | VarPlus Logic | VarPlus Logic | VL6 |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Control Device / PFC Controller / Varlogic | Power quality | Mission Critical | Modbus SL | VarPlus Logic | VL12 |  | NA |  | VPL12N |  | VarPlus Logic | VarPlus Logic | VL12 |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES | NO
Control Device / Speed Drive / ATV | Motor Controller | Mission Critical | Modbus SL | ATV600 | ATV630 |  | NA |  | ATV630xxx |  | ATV600 | ATV600 | ATV630 |  | NA | NA | NA | NA |  | Electricity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through Gateway | YES | NO
Control Device / Speed Drive / ATV | Motor Controller | Mission Critical | Modbus SL | ATV600 | ATV650 |  | NA |  | ATV650yyy |  | ATV600 | ATV600 | ATV650 |  | NA | NA | NA | NA |  | Electricity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through Gateway | YES | NO
Control Device / Speed Drive / ATV | Motor Controller | Mission Critical | Modbus/TCP | ATV600 | ATV630 |  | NA |  | ATV630xxx |  | ATV600 | ATV600 | ATV630 |  | NA | NA | NA | NA |  | Electricity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Control Device / Speed Drive / ATV | Motor Controller | Mission Critical | Modbus/TCP | ATV600 | ATV650 |  | NA |  | ATV650yyy |  | ATV600 | ATV600 | ATV650 |  | NA | NA | NA | NA |  | Electricity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Control Device / Speed Drive / ATV | Motor Controller | Mission Critical | Modbus SL | ATV900 | ATV930 |  | NA |  | ATV930xxx |  | ATV900 | ATV900 | ATV930 |  | NA | NA | NA | NA |  | Electricity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through Gateway | YES | NO
Control Device / Speed Drive / ATV | Motor Controller | Mission Critical | Modbus SL | ATV900 | ATV950 |  | NA |  | ATV950yyy |  | ATV900 | ATV900 | ATV950 |  | NA | NA | NA | NA |  | Electricity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through Gateway | YES | NO
Control Device / Speed Drive / ATV | Motor Controller | Mission Critical | Modbus/TCP | ATV900 | ATV930 |  | NA |  | ATV930xxx |  | ATV900 | ATV900 | ATV930 |  | NA | NA | NA | NA |  | Electricity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Control Device / Speed Drive / ATV | Motor Controller | Mission Critical | Modbus/TCP | ATV900 | ATV950 |  | NA |  | ATV950yyy |  | ATV900 | ATV900 | ATV950 |  | NA | NA | NA | NA |  | Electricity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO
Power Quality Device / Active Harmonic Filter | Power quality | Mission Critical | Modbus SL | Accusine | PCSn |  | NA |  | PCSnxxx |  | Accusine | Accusine | PCSn |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through Gateway | YES ? | NO
Power Quality Device / Active Harmonic Filter | Power quality | Mission Critical | Modbus/TCP | Accusine | PCSn |  | NA |  | PCSnxxx |  | Accusine | Accusine | PCSn |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES ? | NO
Power Quality Device / Active Harmonic Filter | Power quality | Mission Critical | Modbus SL | Accusine | PCS+ |  | NA |  | PCSPyyy |  | Accusine | Accusine | PCS+ |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES ? | NO
Power Quality Device / Active Harmonic Filter | Power quality | Mission Critical | Modbus/TCP | Accusine | PCS+ |  | NA |  | PCSPyyy |  | Accusine | Accusine | PCS+ |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES ? | NO
Power Quality Device / Electronic Reactive Compensation | Power quality | Mission Critical | Modbus SL | Accusine | PFV+ |  | NA |  | EVCPzzz |  | Accusine | Accusine | PFV+ |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Through PaS | YES ? | NO
Power Quality Device / Electronic Reactive Compensation | Power quality | Mission Critical | Modbus/TCP | Accusine | PFV+ |  | NA |  | EVCPzzz |  | Accusine | Accusine | PFV+ |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES ? | NO
Power Quality Device / UPS | Power quality | Mission Critical | Modbus SL | Galaxy | VM (160…1000kVA / 400V) |  | NA |  | GVMxxx |  | Galaxy | Galaxy | VM (160…1000kVA / 400V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus/TCP | Galaxy | VM (160…1000kVA / 400V) |  | NA |  | GVMxxx |  | Galaxy | Galaxy | VM (160…1000kVA / 400V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus SL | Galaxy | VM (160…1125kVA / 480V) |  | NA |  | GVMxxx |  | Galaxy | Galaxy | VM (160…1125kVA / 480V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus/TCP | Galaxy | VM (160…1125kVA / 480V) |  | NA |  | GVMxxx |  | Galaxy | Galaxy | VM (160…1125kVA / 480V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus SL ? | Galaxy | VS (10…50kW / 208V) |  | NA |  | GVSUPSxxx |  | Galaxy | Galaxy | VS (10…50kW / 208V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus/TCP | Galaxy | VS (10…50kW / 208V) |  | NA |  | GVSUPSxxx |  | Galaxy | Galaxy | VS (10…50kW / 208V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus SL ? | Galaxy | VS (10…150kW / 400V) |  | NA |  | GVSUPSxxx |  | Galaxy | Galaxy | VS (10…150kW / 400V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus/TCP | Galaxy | VS (10…150kW / 400V) |  | NA |  | GVSUPSxxx |  | Galaxy | Galaxy | VS (10…150kW / 400V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus SL ? | Galaxy | VS (20…100kW / 480V) |  | NA |  | GVSUPSxxx |  | Galaxy | Galaxy | VS (20…100kW / 480V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus/TCP | Galaxy | VS (20…100kW / 480V) |  | NA |  | GVSUPSxxx |  | Galaxy | Galaxy | VS (20…100kW / 480V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus SL | Galaxy | VX (500…1500kVA / 400V) |  | NA |  | GVXyyy |  | Galaxy | Galaxy | VX (500…1500kVA / 400V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus/TCP | Galaxy | VX (500…1500kVA / 400V) |  | NA |  | GVXyyy |  | Galaxy | Galaxy | VX (500…1500kVA / 400V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus SL | Galaxy | VX (500…1500kVA / 480V) |  | NA |  | GVXyyy |  | Galaxy | Galaxy | VX (500…1500kVA / 480V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Power Quality Device / UPS | Power quality | Mission Critical | Modbus/TCP | Galaxy | VX (500…1500kVA / 480V) |  | NA |  | GVXyyy |  | Galaxy | Galaxy | VX (500…1500kVA / 480V) |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | NA | NO | NO |  |  |  |  | YES
Control Device / PowerLink | Gateway & Server | Mission Critical | Modbus/TCP | PowerLink | G4 3500 |  | NA |  | NF3500G4 |  | PowerLink | PowerLink | G4 3500 |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES ? | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M251 | M251 2x Ethernet |  | NA |  | TM251MESE |  | M251 | M251 | M251 2x Ethernet |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M251 | M251 Ethernet CAN |  | NA |  | TM251MESC |  | M251 | M251 | M251 Ethernet CAN |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M340 | M340 |  | NA |  | BMXP341000 |  | M340 | M340 |  |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M340 | M340 |  | NA |  | BMXP342000 |  | M340 | M340 |  |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M340 | M340 |  | NA |  | BMXP3420102 |  | M340 | M340 |  |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M340 | M340 |  | NA |  | BMXP3420102 |  | M340 | M340 |  |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M340 | M340 |  | NA |  | BMXP3420102CL |  | M340 | M340 |  |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M340 | M340 |  | NA |  | BMXP342020 |  | M340 | M340 |  |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M340 | M340 |  | NA |  | BMXP3420302 |  | M340 | M340 |  |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M340 | M340 |  | NA |  | BMXP3420302CL |  | M340 | M340 |  |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 1 Distributed |  | NA |  | BMEP581020 |  | M580 | M580 | M580 level 1 Distributed |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 2 Distributed |  | NA |  | BMEP582020 |  | M580 | M580 | M580 level 2 Distributed |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 2 Remote |  | NA |  | BMEP582040 |  | M580 | M580 | M580 level 2 Remote |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 3 Distributed |  | NA |  | BMEP583020 |  | M580 | M580 | M580 level 3 Distributed |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 3 Remote |  | NA |  | BMEP583040 |  | M580 | M580 | M580 level 3 Remote |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 4 Distributed |  | NA |  | BMEP584020 |  | M580 | M580 | M580 level 4 Distributed |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 4 Remote |  | NA |  | BMEP584040 |  | M580 | M580 | M580 level 4 Remote |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 5 Remote |  | NA |  | BMEP585040 |  | M580 | M580 | M580 level 5 Remote |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Control Device / PLC | Undefined | Mission Critical | Modbus/TCP | M580 | M580 level 6 Remote |  | NA |  | BMEP586040 |  | M580 | M580 | M580 level 6 Remote |  | NA | NA | NA | NA |  | No Commodity | NA |  |  |  | NA | NA |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA |  |  |  |  | NA | NA | NA | NA | NA |  | Direct | YES | NO |  |  |  |  | YES
Note on BH4: Through PaS Digital Input
Note on BH5: Through PaS Digital Input
Note on BH6: Through PaS Digital Input
Note on BH7: Through PaS Digital Input
Note on BH8: Through PaS Digital Input
Note on BH9: Through PaS Digital Input
Note on BH10: Through PaS Digital Input
Note on BH11: Through PaS Digital Input
Note on BH12: Through PaS Digital Input
Note on BH13: Through PaS Digital Input
Note on BH14: Through PaS Digital Input
Note on BH15: Through PaS Digital Input
Note on BH16: Through PaS Digital Input
Note on BH17: Through PaS Digital Input
Note on BH18: Through PaS Digital Input
Note on BH19: Through PaS Digital Input
Note on BH34: Through PaS Digital Input
Note on BH35: Through PaS Digital Input
Note on BH36: Through PaS Digital Input
Note on BH37: Through PaS Digital Input
Note on BH38: Through PaS Digital Input
Note on BH39: Through PaS Digital Input
Note on BD45: To Be Confirmed by Jean Francois Rolland
Note on BD60: To Be Confirmed by Jean Francois Rolland
Note on BD62: To Be Confirmed by Jean Francois Rolland
Note on BD66: To Be Confirmed by Jean Francois Rolland
Note on BD68: To Be Confirmed by Jean Francois Rolland
Note on BD70: To Be Confirmed by Jean Francois Rolland
Note on BD72: To Be Confirmed by Jean Francois Rolland
Note on BD74: To Be Confirmed by Jean Francois Rolland
Note on BD76: To Be Confirmed by Jean Francois Rolland
Note on BD100: To Be Confirmed by Jean Francois Rolland
Note on BD101: To Be Confirmed by Jean Francois Rolland
Note on BD102: To Be Confirmed by Jean Francois Rolland
Note on BD103: To Be Confirmed by Jean Francois Rolland
Note on BD104: To Be Confirmed by Jean Francois Rolland
Note on BD105: To Be Confirmed by Jean Francois Rolland
Note on BD112: To Be Confirmed with Jean Francois Rolland
Note on BD114: To Be Confirmed with Jean Francois Rolland
Note on BD115: To Be Confirmed with Jean Francois Rolland
Note on BD116: To Be Confirmed with Jean Francois Rolland
Note on BD118: To Be Confirmed with Jean Francois Rolland
Note on BD119: To Be Confirmed with Jean Francois Rolland
Note on BD122: To Be Confirmed with Jean Francois Rolland
Note on BD123: To Be Confirmed with Jean Francois Rolland
Note on L158: ? Pas plus de référence ?
Note on L159: ? Pas plus de référence ?
Note on J281: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Gateway expose this reference instead of the embedded reference (in the FW) = ESST01
Note on J282: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Gateway expose this reference instead of the embedded reference (in the FW) = ESST01
Note on E285: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: HeatTag cable overheating sensor
Note on E286: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: HeatTag cable overheating sensor
Note on E287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: HeatTag cable overheating sensor
Note on E288: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: HeatTag cable overheating sensor
Note on BD477: Not mentioned in the jean Francois Rolland's List
Note on BD478: Not mentioned in the jean Francois Rolland's List
Note on BD481: Not mentioned in the jean Francois Rolland's List
Note on BD482: Not mentioned in the jean Francois Rolland's List
Note on BD485: Not mentioned in the jean Francois Rolland's List

## Data List
METADATA LIST | >>>>> PENDING, DEFINITION IN PROGRESS<<<<<< | COME BACK TO DEVICE LIST
Black: Values from PTI19 SE Invariant | in green: wording evolutions | Black: Values from PTI64 SE Invariant
Black: Values from PTI19 SE Invariant (added for NEMA nrj codes) |  | Blue: Other values from Legacy Solutions (FE)
Blue: Other values from Legacy Solutions (PowerTag Link...)
| in blue = additional fields dedicated for NEC2020 | Commodity List |  | Signal Element List (Digital Input Type) | A-BPaS | SmartLink Modbus Refresh | SmartLink Modbus Legacy | SmartLink SIB Legacy
Usage List | Load Type List | No commodity |  | Circuit breaker status | X | X | X | X
No usage (*) | HVAC System | Electricity |  | Trip elec fault (SDE) | X | X
Air conditionning | Cooler/fridge | Gas |  | Trip fault (SD) | X | X
Compressed Air | Freezer | Fuel oil |  | Trip indicator synthesis | X | X | X | X
Computers | Positive Cold chamber | Air |  | Ground fault | X | X
Cooking | Negative Cold chamber | Steam |  | Earth leakage fault | X | X
Cooling | VRF | Water |  | Insulation fault | X | X
Domestic hot water | AHU | Environment |  | Trip thermal fault (SDT) | X | X
Electrical vehicle charging station | FCU (fan coil unit) | Other |  | Circuit Breaker connected position | X | X
Elevators | Water heater | Custom (Free text to enter) | postponed | Circuit Breaker disconnected position | X | X
Food refrigeration | Ventilator | (*): 'No Commodity' meaning = |  | Circuit Breaker test position | X | X
Genset | Extractor | no defined value: |  | Drawer connected position | X | X
Heating | Rooftop | may be also shown in an UI as |  | Drawer disconnected position | X | X
Heating & Air conditionning | Heatpump | 'blank' or ‘- - - ‘ or 'None' |  | Drawer test position | X | X
Hot sanitary water | Boiler room |  |  | Energy Reduction Maintenance Setting status | X | X
HVAC | Oven |  |  | Voltage loss | X | X
IT | Electric fryer |  |  | Surge arrester fault | X | X
Lighting | Process Loads |  |  | Advanced protection | X | X
Lighting (Interior) | Machine |  |  | Switch position | X | X | X | X
Lighting (Exterior and Park) | Compressor |  |  | Fuse blown | X | X
Loads associated with renewable power source | Pump |  |  | Relay status | X | X
Machine | Water System Pumps |  |  | Trip circuit supervision | X | X | X | X
Main/Incomer | Motor |  |  | Emergency stop | X | X
Mixed usages | Escalator |  |  | Watchdog status | X | X
Office equipment | Elevator |  |  | Source change over - A (Alternate) status | X | X
Plug loads | Light fixture |  |  | Source change over - Off status | X | X
Process | Emergency lighting |  |  | Source change over - N (Normal) status | X | X
Refrigeration | Shutter/Blind |  |  | Motor preheating | X | X
Renewable power source | UPS & IT devices |  |  | Motor run | X | X
Sockets | Cash Register |  |  | Motor start | X | X
Special loads | Neon Sign |  |  | Forced freewheel stop | X | X
Sub/Head of group | Dish Washer / Laundrery |  |  | Battery status | X | X
Total | Receptacle Circuits / Plug Loads |  |  | Battery end of autonomy | X | X
Transportation system (**) | EV Charging Station |  |  | UPS status | X | X
Vapor | Renewable Power Source |  |  | UPS running mode | X | X
Ventilation | Loads Associated with Renewable Power Source |  |  | Auxiliary supply status | X | X | X | X
Water | Building Operations & other Miscellaneous loads |  |  | Tariff 1 Status | X | X
Water system pumps | Non-HVAC Loads |  |  | Tariff 2 Status | X | X
Other / replaced per Custom (Free text to enter) tbc | Industrial / Commercial Load Centers |  |  | Tariff 3 Status | X | X
| Other |  |  | Tariff 4 Status | X | X
(*): 'No Usage' meaning = |  |  |  | Tariff 5 Status | X | X
no defined value: |  |  |  | Door status | X | X | X | X
may be also shown in an UI as |  |  |  | Flood detection | X | X
'blank' or ‘- - - ‘ or 'None' |  |  |  | Under temperature | X | X
|  |  |  | Over temperature | X | X
(**): previoulsy 'Elevator/escalator' |  |  |  | Process Mode | X | X
|  |  |  | Equipment status | X | X
|  |  |  | Fan status | X | X | X | X
|  |  |  | Standard Input Low-High |  |  | X | X
|  |  |  | Standard Input 0-1 |  |  | X | X
|  |  |  | Standard Input 0V-24V |  |  | X | X
|  |  |  | Standard Input Disconnected-Off |  |  |  | X
|  |  | postponed | Custom (Free text to enter) | X | X | X | X
(*): 'No assignement' meaning =
no defined value:
may be also shown in an UI as
'blank' or ‘- - - ‘ or 'None'

## Thermal Sensor data List
ENVIRONMENTAL DEVICE/SENSOR METADATA LIST FOR CONDITION MONITORING (CTM SOLUTION…)
COME BACK TO DEVICE LIST
None': meaning = no defined value: may be shown in an UI as: 'blank' or '- - - ' or …
SELECT DEVICE WITH THE FILTER BELOW:
| Device Type (equipment Type) List | Sensor Position List | Sensor Position List (Json File Format) | Measured Point List | Cubicle ID | Cubicle Type | Circuit Breaker ID | Drawer ID | Cublicle Type (TH110-CL110)
TH110
TH110 | MV Cubicle | MV Cable Connection 1 | MVCableConnection 1 | Phase 1 | None 1 to 34 |  | None 1 to 20 |  | 1 Incomer Or Feeder ACB Or BusTie
TH110 |  |  |  | Phase 2 |  |  |  |  | 2 Incomers
TH110 |  |  |  | Phase 3 |  |  |  |  | 1 Incomer + 1 BusTie
TH110 |  | MV Cable Connection 2 | MVCableConnection 2 | Phase 1 | None 1 to 34 |  | None 1 to 20 |  | 3 Feeders ACBs
TH110 |  |  |  | Phase 2 |  |  |  |  | 1 Incomer + 2 Feeder ACBs
TH110 |  |  |  | Phase 3 |  |  |  |  | 2 Incomers + 1 Bus Tie
TH110 |  | CB Lower Arms | CBLowerArms | Phase 1 | None 1 to 34 |  | None 1 to 20 |  | Feeder MCCBs + Drawers
TH110 |  |  |  | Phase 2 |  |  |  |  | 1 Incomer + Feeder MCCBs
TH110 |  |  |  | Phase 3 |  |  |  |  | Drawers
TH110 |  | CB Upper Arms | CBUpperArms | Phase 1 | None 1 to 34 |  | None 1 to 20 |  | Feeder MCCBs
TH110 |  |  |  | Phase 2 |  |  |  |  | 4 Feeders ACBs
TH110 |  |  |  | Phase 3 |  |  |  |  | None (*)
TH110 |  | Bus Bar Connection 1 | BusBarConnection1 | Phase 1 | None 1 to 34 |  | None 1 to 20
TH110 |  |  |  | Phase 2 |  |  |  |  | (*): 'None' meaning =
TH110 |  |  |  | Phase 3 |  |  |  |  | no defined value:
TH110 |  | Bus Bar Connection 2 | BusBarConnection2 | Phase 1 | None 1 to 34 |  | None 1 to 20 |  | may be shown in an UI as
TH110 |  |  |  | Phase 2 |  |  |  |  | blank' or ‘- - - ‘ or…
TH110 |  |  |  | Phase 3
TH110 |  | Other | Other | Phase 1
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  |  |  | Other
TH110 | MV/LV Transformer | MV Cable Connection 1 | TFO_MVCableConnection1 | Phase 1 | None 1 to 34 |  | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  | LV Cable Connection | TFO_LVCableConnection | Phase 1 | None 1 to 34 |  | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | Winding Connection | TFO_WindingConnection | Phase 1 | None 1 to 34 |  | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  | Tapping Link Connection | TFO_TappingLinkConnection | Phase 1 | None 1 to 34 |  | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  | Other | TFO_Other | Phase 1
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  |  |  | Other
TH110 | LV Switchboard | LV Customer Connection 1 | LVCustomerConnection1 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Customer Connection 2 | LVCustomerConnection2 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Incomer CB Downstream 1 | LVIncomerCBDownstream1 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Incomer CB Downstream 2 | LVIncomerCBDownstream2 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Incomer CB Upstream 1 | LVIncomerCBUpstream1 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Incomer CB Upstream 2 | LVIncomerCBUpstream2 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV HBB-VBB Joint 1 | LVHBB_VBBJoint1 | Phase 1 | None 1 to 34 | Cubicle Type List
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV HBB-VBB Joint 2 | LVHBB_VBBJoint2 | Phase 1 | None 1 to 34 | Cubicle Type List
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Splice Bar 1 | LVSpliceBar1 | Phase 1 | None 1 to 34 | Cubicle Type List
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Splice Bar 2 | LVSpliceBar2 | Phase 1 | None 1 to 34 | Cubicle Type List
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Feeder MCCB Loads | LVFeederMCCBLoads | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Bus Tie Upstream 1 | LVBusTieUpstream1 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Bus Tie Upstream 2 | LVBusTieUpstream2 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Bus Tie Downstream 1 | LVBusTieDownstream1 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Bus Tie Downstream 2 | LVBusTieDownstream2 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Feeder CB Upstream 1 | LVFeederCBUpstream1 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Feeder CB Upstream 2 | LVFeederCBUpstream2 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Feeder CB Downstream 1 | LVFeederCBDownstream1 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | LV Feeder CB Downstream 2 | LVFeederCBDownstream2 | Phase 1 | None 1 to 34 | Cubicle Type List | None 1 to 20
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  | Other | Other | Phase 1
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  |  |  | Other
TH110 | Other | Other | Other | Phase 1
TH110 |  |  |  | Phase 2
TH110 |  |  |  | Phase 3
TH110 |  |  |  | Neutral
TH110 |  |  |  | Other
CL110
CL110 | MV Cubicle | LV Cabinet | LVCabinet | Ambient | None 1 to 34
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 |  | Bus Bar Cabinet | BusBarCabinet | Ambient | None 1 to 34
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 |  | CB Cabinet | CBCabinet | Ambient | None 1 to 34
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 |  | Cable Cabinet | CableCabinet | Ambient | None 1 to 34
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 |  | Other | Other | Phase 1
CL110 |  |  |  | Phase 2
CL110 |  |  |  | Phase 3
CL110 |  |  |  | 3 Phases
CL110 |  |  |  | Neutral
CL110 |  |  |  | Ambient
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 | MV/LV Transformer | Transformer Ambient | TFO_Ambient | Ambient | None 1 to 34
CL110 |  | Other | Other | Phase 1
CL110 |  |  |  | Phase 2
CL110 |  |  |  | Phase 3
CL110 |  |  |  | 3 Phases
CL110 |  |  |  | Neutral
CL110 |  |  |  | Ambient
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 | LV Switchboard | LV Cable Compartment | LVCableCompartment | Ambient | None 1 to 34 | Cubicle Type List
CL110 |  | LV Drawer | LVDrawer | Ambient | None 1 to 34 | Cubicle Type List |  | None 1 to 20
CL110 |  | Other | Other | Phase 1
CL110 |  |  |  | Phase 2
CL110 |  |  |  | Phase 3
CL110 |  |  |  | 3 Phases
CL110 |  |  |  | Neutral
CL110 |  |  |  | Ambient
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 | Busway | Busway | Busway | Phase 1
CL110 |  |  |  | Phase 2
CL110 |  |  |  | Phase 3
CL110 |  |  |  | 3 Phases
CL110 |  |  |  | Neutral
CL110 |  |  |  | Ambient
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 | Electrical Room | Room | Room | Ambient
CL110 |  |  |  | Other
CL110 |  | Other | Other | Phase 1
CL110 |  |  |  | Phase 2
CL110 |  |  |  | Phase 3
CL110 |  |  |  | 3 Phases
CL110 |  |  |  | Neutral
CL110 |  |  |  | Ambient
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
CL110 | Other | Other | Other | Phase 1
CL110 |  |  |  | Phase 2
CL110 |  |  |  | Phase 3
CL110 |  |  |  | 3 Phases
CL110 |  |  |  | Neutral
CL110 |  |  |  | Ambient
CL110 |  |  |  | Cold point
CL110 |  |  |  | Other
SMT10020 (HeatTag)
SMT10020 (HeatTag) | LV Switchboard | LV Column |  | Ambient | None 1 to 34 | Incomer
SMT10020 (HeatTag) | [5 empty] | Incomer And Feeders
SMT10020 (HeatTag) | [5 empty] | Feeders
SMT10020 (HeatTag) | [5 empty] | Distribution
SMT10020 (HeatTag) |  | LV Cable Compartment |  | Ambient | None 1 to 34 1 to 20 | Cable Compartment
SMT10020 (HeatTag) | [5 empty] | Outgoing Terminal
SMT10020 (HeatTag) |  | LV Drawer |  | Ambient | None 1 to 34 | Drawers |  | None 1 to 20
SMT10020 (HeatTag)
SMT10020 (HeatTag) |  | Other |  | Ambient
PD100 (PD Box)
PD100 (PD Box) | MV Cubicle |  |  |  | None 1 to 34 |  | None 1 to 20
PD100 (PD Box)
PD100 (PD Box)

## PREDEFINED EVENTS
Device | Device (Details) | Identification |  |  |  | Triggers |  |  | Periodic check Rate (s) | Publication Rate (s) | Inhibit | Context | Characterization |  |  |  | Comments
|  | Event Code | Type | PDM Short Name ID (aca Event ID, Event Code) | Full Name | Trigger Type | Trigger | Detection Rate (s) |  |  |  |  | Category | Severity | FE Notification | Used for context
PowerTag Energy
PowerTag Energy | PowerTags I60, M63 PowerTags P63 (DT40…) PowerTags Flex (aca DT40+Vigi), F63 PowerTags NSX PowerTags Square D QO PowerTags Square D Q&B PowerTags Square D E Frame PowerTag 160A PowerTags Square D H,J,L Frame PowerTags Rope
PowerTag Energy |  | CALH1_VLoss3PhsAlm | Vloss Status | CALH1_VLoss3PhsAlm | Voltage loss 3 phases status alarm | Unique | CALH1_VLoss3PhsAlm | 60 | na | asap |  | IA IB IC LPHD1_CircuitProtectionRatingCurrent | Complex | High | Yes | No
PowerTag Energy |  | CALH1_CommLoss | Communication | CALH1_CommLoss | Communication Loss | Unique | CALH1_CommLoss | 180 | na | asap |  |  | Simple | Low | Yes | No
PowerTag C 2DI
PowerTag C 2DI |  | DiIn_GGIO1_XCBR1_Pos1 | OF Status | DiIn_GGIO1_XCBR1_Pos1 | OF Status | Unique | DiIn_GGIO1_XCBR1_Pos1 | 60 | na | asap |  |  | Simple | Low | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | DiIn_GGIO1_XCBR1_CBTripInd1 | Trip Status | DiIn_GGIO1_XCBR1_CBTripInd1 | SD Status | Unique | DiIn_GGIO1_XCBR1_CBTripInd1 | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | DiIn_GGIO1_XCBR1_Pos2 | OF Status | DiIn_GGIO1_XCBR1_Pos2 | OF Status | Unique | DiIn_GGIO1_XCBR1_Pos2 | 60 | na | asap |  |  | Simple | Low | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | DiIn_GGIO1_XCBR1_CBTripInd2 | Trip Status | DiIn_GGIO1_XCBR1_CBTripInd2 | SD Status | Unique | DiIn_GGIO1_XCBR1_CBTripInd2 | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | DiIn_GGIO1_XCBR1_CBTripInd2 | Trip Status | DiIn_GGIO1_Ind1 | Standard Input | Unique | DiIn_GGIO1_Ind1 | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | DiIn_GGIO1_XCBR1_CBTripInd2 | Trip Status | DiIn_GGIO1_Ind1 | Standard Input | Unique | DiIn_GGIO1_Ind1 | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | To Modelize | Trip Status | To Modelize | Chained SD | Unique |  | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_BatAutonomyAlm | UPS Battery Status | CALH1_BatAutonomyAlm | Battery End Of Autonomy | Unique | CALH1_BatAutonomyAlm | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_BatAlm | UPS Battery Status | CALH1_BatAlm | Battery End Of Life | Unique | CALH1_BatAlm | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | XCBR1_TripSuperv | Trip Status | XCBR1_TripSuperv | Circuit Supervion | Unique | XCBR1_TripSuperv | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | GGIO1_DoorSt | Door Status | GGIO1_DoorSt | Door Status | Unique | GGIO1_DoorSt | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_FloodDetectionAlm | Flood Detection | CALH1_FloodDetectionAlm | Flood Detection | Unique | CALH1_FloodDetectionAlm | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_FuseAlm | Fuse Status | CALH1_FuseAlm | Fuse Status | Unique | CALH1_FuseAlm | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_VLossAlm | Vloss Status | CALH1_VLossAlm | Input Voltage Presence | Unique | CALH1_VLossAlm | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | OverTAlr | Temperature Status | OverTAlr | Over Temperature | Unique | OverTAlr | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_RelayAlm | Relay Status | CALH1_RelayAlm | Relay Status | Unique | CALH1_RelayAlm | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | GGIO1_SwitchSt | Switch Status | GGIO1_SwitchSt | Switch Status | Unique | GGIO1_SwitchSt | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | UnderTAlr | Temperature Status | UnderTAlr | Under Temperature | Unique | UnderTAlr | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | GGIO1_UPSMode | UPS Mode | GGIO1_UPSMode | UPS Mode | Unique | GGIO1_UPSMode | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_UPSAlm | UPS Status | CALH1_UPSAlm | UPS Status | Unique | CALH1_UPSAlm | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_WatchdogAlm | Watchdog | CALH1_WatchdogAlm | Watchdog | Unique | CALH1_WatchdogAlm | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | To Modelize | Surge Status | To Modelize | Surge Failure Contact | Unique |  | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the input configuration
PowerTag C 2DI |  | CALH1_CommLoss | Communication | CALH1_CommLoss | Communication Loss | Unique | CALH1_CommLoss | 180 | na | asap |  |  | Simple | Low | Yes | No | activated if an event is selected
Wireless OF/SD (aka ZAC-Quazar)
Wireless OF/SD (aka ZAC-Quazar) |  | XCBR1_Pos | OF Status | XCBR1_Pos | OF Status | Unique | XCBR1_Pos | 60 | na | asap |  |  | Simple | Low | Yes | No | predefined event selected in the list during the Wireless OF/SD Configuration
Wireless OF/SD (aka ZAC-Quazar) |  | XCBR1_CBTripInd | Trip Status | XCBR1_CBTripInd | SD Status | Unique | XCBR1_CBTripInd | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the Wireless OF/SD Configuration
Wireless OF/SD (aka ZAC-Quazar) |  | XCBR1_CBElecTripInd | Trip Status | XCBR1_CBElecTripInd | SDE Status | Unique | XCBR1_CBElecTripInd | 60 | na | asap |  |  | Simple | High | Yes | No | predefined event selected in the list during the Wireless OF/SD Configuration
Wireless OF/SD (aka ZAC-Quazar) |  | CALH1_BatPreAlm | Battery Alarm | CALH1_BatPreAlm | Battery Pre-Alarm | Unique | XCBR1_Pos XCBR1_CBTripInd XCBR1_CBElecTripInd | 60 | 28800 | asap |  |  | Simple | High | Yes | No | predefined event activated if OF-SD-SDE event has been selected in the list during the Wireless OF/SD Configuration
Wireless OF/SD (aka ZAC-Quazar) |  | CALH1_BatAlm | Battery Alarm | CALH1_BatAlm | Replace Battery | Unique | XCBR1_Pos XCBR1_CBTripInd XCBR1_CBElecTripInd | 60 | 28800 | asap |  |  | Simple | High | Yes | No | predefined event activated if OF-SD-SDE event has been selected in the list during the Wireless OF/SD Configuration
Wireless OF/SD (aka ZAC-Quazar) |  | CALH1_CommLoss | Communication | CALH1_CommLoss | Communication Loss | na | na | 259200 | na | asap |  |  | Simple | Low | Yes | No | Activated if OF-SD-SDE event has been selected in the list during the Wireless OF/SD Configuration Detetection rate: based on the fact that 9 subsequent publications are lost (9*8h = 72h = 259200s)
MCCB Breakers / µLogic NSX & HJL
MCCB Breakers / µLogic NSX & HJL | Compact NSX - µLogic NSX A-E PowerPact HJL - µLogic NSX A-E
MCCB Breakers / µLogic NSX & HJL |  | XCBR1_CBTripInd | Trip unit status | XCBR1_CBTripInd | SD Status | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos | Complex | High | Yes | Yes
MCCB Breakers / µLogic NSX & HJL |  | XCBR1_CBElecTripInd | Trip unit status | XCBR1_CBElecTripInd | SDE Status | Events Group | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos | Complex | High | Yes | No
MCCB Breakers / µLogic NSX & HJL |  | LT_PTOC1_Op | Trip unit status | LT_PTOC1_Op | Long Time (LT) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBTripInd LT_PTOC1_OpCntRs Trip_GLOG1_EntryTripSwA Trip_GLOG1_EntryTripOrigin SCBR1_AccAbr | Complex | High | Yes | No
MCCB Breakers / µLogic NSX & HJL |  | ST_PTOC1_Op | Trip unit status | ST_PTOC1_Op | Short Time (ST) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBTripInd ST_PTOC1_OpCntRs Trip_GLOG1_EntryTripSwA Trip_GLOG1_EntryTripOrigin SCBR1_AccAbr | Complex | High | Yes | No
MCCB Breakers / µLogic NSX & HJL |  | PIOC1_Op | Trip unit status | PIOC1_Op | Instantaneous (I) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBTripInd PIOC1_OpCntRs Trip_GLOG1_EntryTripSwA Trip_GLOG1_EntryTripOrigin SCBR1_AccAbr | Complex | High | Yes | No
MCCB Breakers / µLogic NSX & HJL |  | G_PTOC1_Op | Trip unit status | G_PTOC1_Op | Ground Fault (GF) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBTripInd G_PTOC1_OpCntRs Trip_GLOG1_EntryTripSwA Trip_GLOG1_EntryTripOrigin SCBR1_AccAbr | Complex | High | Yes | No
MCCB Breakers / µLogic NSX & HJL |  | EF_PTOC1_Op | Trip unit status | EF_PTOC1_Op | Earth Fault (EF) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBTripInd EF_PTOC1_OpCntRs Trip_GLOG1_EntryTripSwA Trip_GLOG1_EntryTripOrigin SCBR1_AccAbr | Complex | High | Yes | No | µLogic NSX E Only
MCCB Breakers / µLogic NSX & HJL |  | PIOC2_Op | Trip unit status | PIOC2_Op | Integrated Inst. Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBTripInd Trip_GLOG1_EntryTripSwA Trip_GLOG1_EntryTripOrigin | Complex | High | Yes | No
MCCB Breakers / µLogic NSX & HJL |  | LT_PTOC2_OpReq | Pre Alarm | LT_PTOC2_OpReq | Long Time (LT) Pre Alarm | Unique | LT_PTOC2_OpReq | 30 | na | asap |  |  | Simple | Low | Yes | No | Simple event which generate a notification in FE
MCCB Breakers / µLogic NSX & HJL |  | G_PTOC2_OpReq | Pre Alarm | G_PTOC2_OpReq | Ground Fault (GF) Pre Alarm | Unique | G_PTOC2_OpReq | 30 | na | asap |  |  | Simple | Low | Yes | No | Simple event which generate a notification in FE
MCCB Breakers / µLogic NSX & HJL |  | XCBR1_Pos | Trip unit status | XCBR1_Pos | OF Status | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | Low | Yes | Yes
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_TripUnitFail | Trip unit status | LPHD1_TripUnitFail | Trip Unit internal failure | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | High | No | No
MCCB Breakers / µLogic NSX & HJL |  | XCBR1_CBElecTripCntRs | Trip Counter | XCBR1_CBElecTripCntRs | Trip counter (SDE) | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | Trip_GLOG1_EntryTripSwA | Trip switched current | Trip_GLOG1_EntryTripSwA | Interrupted current (peak) | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | Trip_GLOG1_EntryTripOrigin |  | Trip_GLOG1_EntryTripOrigin | Entry Trip Origin | [9 empty] | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | SCBR1_AccAbr | Breaker contact abrasion | SCBR1_AccAbr | Breaker Contact Wear | Events Group | XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | LT_PTOC1_OpCntRs | Trip Counter | LT_PTOC1_OpCntRs | Long Time Trip counter | Events Group | XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | ST_PTOC1_OpCntRs | Trip Counter | ST_PTOC1_OpCntRs | Short Time Trip counter | Events Group | XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | PIOC1_OpCntRs | Trip Counter | PIOC1_OpCntRs | Instantaneous Trip counter | Events Group | XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | G_PTOC1_OpCntRs | Trip Counter | G_PTOC1_OpCntRs | Ground Fault Trip counter | Events Group | XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | EF_PTOC1_OpCntRs | Trip Counter | EF_PTOC1_OpCntRs | Earth Fault Trip counter | Events Group | XCBR1_CBTripCntRs | 15 | 86400 | asap |  |  | Simple | None | No | Yes | µlogic NSX E only
MCCB Breakers / µLogic NSX & HJL |  | XCBR1_CBClsPosCnt | Breaker number of cycles | XCBR1_CBClsPosCnt | Breaker number of cycles | Unique | XCBR1_CBClsPosCnt | 15 | na | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | XCBR1_CBTripCntRs | Trip Counter | XCBR1_CBTripCntRs | Trip counter (SD) | Unique | XCBR1_CBTripCntRs | 15 | na | asap |  |  | Simple | None | No | Yes
MCCB Breakers / µLogic NSX & HJL |  | G_PTOC1_Crv | Ground Fault protection setting | G_PTOC1_Crv | Ground Fault (GF): I2t ON/OFF curve setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | G_PTOC1_Mod | Ground Fault protection setting | G_PTOC1_Mod | Ground Fault (GF) Protection ON | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | G_PTOC1_OpDlTm | Ground Fault protection setting | G_PTOC1_OpDlTm | Ground Fault (GF): Delay (tg) setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | G_PTOC1_StrVal | Ground Fault protection setting | G_PTOC1_StrVal | Ground Fault (GF): Pick-Up Value (Ig) setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_ApplicationType | Device Type | LPHD1_ApplicationType | Application Type | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_Artg | Rated Current | LPHD1_Artg | Rated current | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_FwRev | Firmware Revision | LPHD1_FwRev | Firmware Revision | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_HwRev | Hardware Revision | LPHD1_HwRev | Hardware Revision | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_MeteringType | Device Type | LPHD1_MeteringType | Metering Type | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_PolesNum | Number of Poles | LPHD1_PolesNum | Number of Poles | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_ProtectionType | Protection Type | LPHD1_ProtectionType | Protection Type | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_SerNum | Serial Number | LPHD1_SerNum | Serial Number | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LPHD1_VRtg | Rated Voltage | LPHD1_VRtg | Rated Voltage | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LT_PTOC1_Mod | Long Time protection setting | LT_PTOC1_Mod | Long Time (LT) Protection ON | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LT_PTOC1_OpDlTm | Long Time protection setting | LT_PTOC1_OpDlTm | Long Time (LT): Delay (tr) setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LT_PTOC1_StrVal | Long Time protection setting | LT_PTOC1_StrVal | Long Time (LT): Pick-Up Value (Ir) setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | LT_PTOC2_StrValCoef | Long Time protection setting | LT_PTOC2_StrValCoef | Pre alarm in % of Ir pick-up value | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | PIOC1_Mod | Instantaneous protection setting | PIOC1_Mod | Instantaneous (Ii) Protection ON | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | PIOC1_StrVal | Instantaneous protection setting | PIOC1_StrVal | Instantaneous: Pick-Up Value (Ii) setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | ST_PTOC1_Crv | Short Time protection setting | ST_PTOC1_Crv | Short Time (ST): I2t ON/OFF curve setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | ST_PTOC1_Mod | Short Time protection setting | ST_PTOC1_Mod | Short Time (ST) Protection ON | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | ST_PTOC1_OpDlTm | Short Time protection setting | ST_PTOC1_OpDlTm | Short Time (ST): Delay (tsd) setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | ST_PTOC1_StrVal | Short Time protection setting | ST_PTOC1_StrVal | Short Time (ST): Pick-Up Value (Isd) setting | Events Group | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
MCCB Breakers / µLogic NSX & HJL |  | Maint_GLOG1_EntryEvtDT | Maintenance operation date time | Maint_GLOG1_EntryEvtDT | Maintenance operation date time | Unique | Maint_GLOG1_EntryEvtDT | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers µlogic Compact Masterpact Powerpact
ACB Breakers µlogic Compact Masterpact Powerpact | Compact NS/PowerPact MPR - µLogic E-P Masterpact NT-NW - µLogic E-P
ACB Breakers µlogic Compact Masterpact Powerpact |  | XCBR1_CBTripInd | Trip unit status | XCBR1_CBTripInd | SD Status | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_Pos | Complex | High | Yes | No
ACB Breakers µlogic Compact Masterpact Powerpact |  | XCBR1_CBElecTripInd | Trip unit status | XCBR1_CBElecTripInd | SDE Status | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos | Complex | High | Yes | Yes
ACB Breakers µlogic Compact Masterpact Powerpact |  | LT_PTOC1_Op | Trip unit status | LT_PTOC1_Op | Long Time (LT) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers µlogic Compact Masterpact Powerpact |  | ST_PTOC1_Op | Trip unit status | ST_PTOC1_Op | Short Time (ST) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers µlogic Compact Masterpact Powerpact |  | PIOC1_Op | Trip unit status | PIOC1_Op | Instantaneous (I) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers µlogic Compact Masterpact Powerpact |  | G_PTOC1_Op | Trip unit status | G_PTOC1_Op | Ground Fault (GF) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers µlogic Compact Masterpact Powerpact |  | EF_PTOC1_Op | Trip unit status | EF_PTOC1_Op | Earth Fault (EF) Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers µlogic Compact Masterpact Powerpact |  | PIOC2_Op | Trip unit status | PIOC2_Op | Integrated Inst. Trip | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers µlogic Compact Masterpact Powerpact |  | XCBR1_Pos | Trip Unit Status | XCBR1_Pos | OF Status | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  |  | Simple | None | Yes | Yes
ACB Breakers µlogic Compact Masterpact Powerpact |  | LPHD1_TripUnitFail | Trip unit status | LPHD1_TripUnitFail | Trip Unit internal failure | Events Group | XCBR1_CBClsPosCnt XCBR1_CBTripCntRs XCBR1_CBElecTripCntRs | 15 | 86400 | asap |  |  | Simple | High | No | No
ACB Breakers µlogic Compact Masterpact Powerpact |  | XCBR1_CBClsPosCnt | Breaker number of cycles | XCBR1_CBClsPosCnt | Breaker number of cycles | Unique | XCBR1_CBClsPosCnt | 15 | na | asap |  |  | Simple | None | No | Yes
ACB Breakers µlogic Compact Masterpact Powerpact |  | XCBR1_CBTripCntRs | Trip Counter | XCBR1_CBTripCntRs | Trip counter (SD) | Unique | XCBR1_CBTripCntRs | 15 | na | asap |  |  | Simple | None | No | Yes
ACB Breakers µlogic Compact Masterpact Powerpact |  | XCBR1_CBElecTripCntRs | Trip Counter | XCBR1_CBElecTripCntRs | Trip counter (SDE) | Unique | XCBR1_CBElecTripCntRs | 15 | na | asap |  |  | Simple | None | No | Yes
ACB Breakers µlogic Compact Masterpact Powerpact |  | EF_PTOC1_Mod | Earth Fault protection setting | EF_PTOC1_Mod | Earth Fault (EF) Protection ON | na | EF_PTOC1_Mod | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | EF_PTOC1_OpDlTm | Earth Fault protection setting | EF_PTOC1_OpDlTm | Earth Fault (EF): Delay (t∆n) setting | na | EF_PTOC1_OpDlTm | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | EF_PTOC1_StrVal | Earth Fault protection setting | EF_PTOC1_StrVal | Earth Fault (EF): Pick-Up Value (I∆n) setting | na | EF_PTOC1_StrVal | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | G_PTOC1_Crv | Ground Fault protection setting | G_PTOC1_Crv | Ground Fault (GF): I2t ON/OFF curve setting | na | G_PTOC1_Crv | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | G_PTOC1_Mod | Ground Fault protection setting | G_PTOC1_Mod | Ground Fault (GF) Protection ON | na | G_PTOC1_Mod | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | G_PTOC1_OpDlTm | Ground Fault protection setting | G_PTOC1_OpDlTm | Ground Fault (GF): Delay (tg) setting | na | G_PTOC1_OpDlTm | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | G_PTOC1_StrVal | Ground Fault protection setting | G_PTOC1_StrVal | Ground Fault (GF): Pick-Up Value (Ig) setting | na | G_PTOC1_StrVal | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LPHD1_Artg | Rated Current | LPHD1_Artg | Rated current | na | LPHD1_Artg | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LPHD1_BatCharRte | Battery Charge | LPHD1_BatCharRte | Battery Charge | na | LPHD1_BatCharRte | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LPHD1_FwRev | Firmware Revision | LPHD1_FwRev | Firmware Revision | na | LPHD1_FwRev | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LPHD1_MeteringType | Device Type | LPHD1_MeteringType | Metering Type | na | LPHD1_MeteringType | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LPHD1_ProtectionType | Protection Type | LPHD1_ProtectionType | Protection Type | na | LPHD1_ProtectionType | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LPHD1_SerNum | Serial Number | LPHD1_SerNum | Serial Number | na | LPHD1_SerNum | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LPHD1_VRtg | Rated Voltage | LPHD1_VRtg | Rated Voltage | na | LPHD1_VRtg | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LT_PTOC1_Mod | Long Time protection setting | LT_PTOC1_Mod | Long Time (LT) Protection ON | na | LT_PTOC1_Mod | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LT_PTOC1_OpDlTm | Long Time protection setting | LT_PTOC1_OpDlTm | Long Time (LT): Delay (tr) setting | na | LT_PTOC1_OpDlTm | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | LT_PTOC1_StrVal | Long Time protection setting | LT_PTOC1_StrVal | Long Time (LT): Pick-Up Value (Ir) setting | na | LT_PTOC1_StrVal | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | PIOC1_Mod | Instantaneous protection setting | PIOC1_Mod | Instantaneous (Ii) Protection ON | na | PIOC1_Mod | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | PIOC1_StrVal | Instantaneous protection setting | PIOC1_StrVal | Instantaneous: Pick-Up Value (Ii) setting | na | PIOC1_StrVal | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | SCBR1_AccAbrNeut | Breaker contact abrasion | SCBR1_AccAbrNeut | Breaker contact abrasion neutral | na | SCBR1_AccAbrNeut | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | SCBR1_AccAbrPhsA | Breaker contact abrasion | SCBR1_AccAbrPhsA | Breaker contact abrasion phase A | na | SCBR1_AccAbrPhsA | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | SCBR1_AccAbrPhsB | Breaker contact abrasion | SCBR1_AccAbrPhsB | Breaker contact abrasion phase B | na | SCBR1_AccAbrPhsB | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | SCBR1_AccAbrPhsAC | Breaker contact abrasion | SCBR1_AccAbrPhsAC | Breaker contact abrasion phase C | na | SCBR1_AccAbrPhsAC | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | ST_PTOC1_Crv | Short Time protection setting | ST_PTOC1_Crv | Short Time (ST): I2t ON/OFF curve setting | na | ST_PTOC1_Crv | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | ST_PTOC1_Mod | Short Time protection setting | ST_PTOC1_Mod | Short Time (ST) Protection ON | na | ST_PTOC1_Mod | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | ST_PTOC1_OpDlTm | Short Time protection setting | ST_PTOC1_OpDlTm | Short Time (ST): Delay (tsd) setting | na | ST_PTOC1_OpDlTm | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers µlogic Compact Masterpact Powerpact |  | ST_PTOC1_StrVal | Short Time protection setting | ST_PTOC1_StrVal | Short Time (ST): Pick-Up Value (Isd) setting | na | ST_PTOC1_StrVal | na | na | 86400 |  |  | Simple | None | No | No | No trigger available, periodic publication
ACB Breakers Masterpact MTZ - µLogic X
ACB Breakers Masterpact MTZ - µLogic X |  | XCBR1_CBTripInd | SD | XCBR1_CBTripInd | SD Status | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | Complex | High | Yes | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | XCBR1_CBElecTripInd | SDE | XCBR1_CBElecTripInd | SDE Status | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | SCBR1_OpCnt, XCBR1_Pos, XCBR1_CBTripInd, Trip_GLOG1_TripOpCnt, Trip_GLOG1_TripOpLTCnt, Trip_GLOG1_TripOpSTCnt, Trip_GLOG1_TripOpICnt, Trip_GLOG1_TripOpGEFCnt, Trip_GLOG1_LastEvt_SwAPhsA, Trip_GLOG1_LastEvt_SwAPhsB, Trip_GLOG1_LastEvt_SwAPhsC, Trip_GLOG1_LastEvt_SwANeut, SCBR1_AccAbrPhsA, SCBR1_AccAbrPhsB, SCBR1_AccAbrPhsC, SCBR1_AccAbrNeut, Trip_GLOG1_LastEvtCode, | Complex | High | Yes | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | LT_PTOC1_Op | Trip unit status | LT_PTOC1_Op | Long Time (LT) Trip | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers Masterpact MTZ - µLogic X |  | ST_PTOC1_Op | Trip unit status | ST_PTOC1_Op | Short Time (ST) Trip | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers Masterpact MTZ - µLogic X |  | PIOC1_Op | Trip unit status | PIOC1_Op | Instantaneous (I) Trip | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers Masterpact MTZ - µLogic X |  | G_PTOC1_Op | Trip unit status | G_PTOC1_Op | Ground Fault (GF) Trip | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers Masterpact MTZ - µLogic X |  | EF_PTOC1_Op | Trip unit status | EF_PTOC1_Op | Earth Fault (EF) Trip | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers Masterpact MTZ - µLogic X |  | SELLIM_PIOC1_Op | Trip unit status | SELLIM_PIOC1_Op | Ultimate self-protection trip (SELLIM) | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers Masterpact MTZ - µLogic X |  | DIN_PIOC1_Op | Trip unit status | DIN_PIOC1_Op | Ultimate self-protection trip (DIN/DINF) | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt, XCBR1_Pos | 15 | 86400 | asap |  | XCBR1_CBClsPosCnt XCBR1_CBElecTripCntRs XCBR1_Pos XCBR1_CBElecTripInd | Complex | High | Yes | No
ACB Breakers Masterpact MTZ - µLogic X |  | XCBR1_Pos | OF | XCBR1_Pos | OF | Events Group | SCBR1_OpCnt, Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | Low | Yes | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | SCBR1_OpCnt | Breaker number of cycles | SCBR1_OpCnt | Breaker number of cycles | Unique | SCBR1_OpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | Trip_GLOG1_TripOpCnt | Trip Counter | Trip_GLOG1_TripOpCnt | Trip counter (SDE) | Unique | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | Trip_GLOG1_TripOpLTCnt | Trip Counter | Trip_GLOG1_TripOpLTCnt | Trip counter (LT) | Events Group | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | Trip_GLOG1_TripOpSTCnt | Trip Counter | Trip_GLOG1_TripOpSTCnt | Trip counter (ST) | Events Group | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | Trip_GLOG1_TripOpICnt | Trip Counter | Trip_GLOG1_TripOpICnt | Trip counter (I) | Events Group | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | Trip_GLOG1_TripOpGEFCnt | Trip Counter | Trip_GLOG1_TripOpGEFCnt | Trip counter (GF) | Events Group | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | SCBR1_AccAbrPhsA | Contact Wear | SCBR1_AccAbrPhsA | PhaseContactWear A | Events Group | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | SCBR1_AccAbrPhsB | Contact Wear | SCBR1_AccAbrPhsB | PhaseContactWear B | Events Group | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | SCBR1_AccAbrPhsC | Contact Wear | SCBR1_AccAbrPhsC | PhaseContactWear C | Events Group | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | SCBR1_AccAbrNeut | Contact Wear | SCBR1_AccAbrNeut | PhaseContactWear N | Events Group | Trip_GLOG1_TripOpCnt | 15 | 86400 | asap |  |  | Simple | None | No | Yes
ACB Breakers Masterpact MTZ - µLogic X |  | LPHD1_ARtg | Rated current | LPHD1_ARtg | Rated current | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | LT_PTOC1_Mod | Long Time protection setting | LT_PTOC1_Mod | Long Time (LT) Protection ON | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | LT_PTOC1_StrVal | Long Time protection setting | LT_PTOC1_StrVal | Long Time (LT): Pick-Up Value (Ir) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | LT_PTOC1_OpDlTm | Long Time protection setting | LT_PTOC1_OpDlTm | Long Time (LT): Delay (tr) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | ST_PTOC1_Mod | Short Time protection setting | ST_PTOC1_Mod | Short Time (ST) Protection ON | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | ST_PTOC1_Crv | Short Time protection setting | ST_PTOC1_Crv | Short Time (ST): I2t ON/OFF curve setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | ST_PTOC1_StrValCoef | Short Time protection setting | ST_PTOC1_StrValCoef | Short Time (ST): Pick-Up Value (Isd) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | ST_PTOC1_OpDlTm | Short Time protection setting | ST_PTOC1_OpDlTm | Short Time (ST): Delay (tsd) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | PIOC1_Mod | Instantaneous protection setting | PIOC1_Mod | Instantaneous (Ii) Protection ON | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | PIOC1_StrValCoef | Instantaneous protection setting | PIOC1_StrValCoef | Instantaneous: Pick-Up Value (Ii) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | G_PTOC1_Mod | Ground Fault protection setting | G_PTOC1_Mod | Ground Fault (GF) Protection ON | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | G_PTOC1_Crv | Ground Fault protection setting | G_PTOC1_Crv | Ground Fault (GF): I2t ON/OFF curve setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | G_PTOC1_StrVal | Ground Fault protection setting | G_PTOC1_StrVal | Ground Fault (GF): Pick-Up Value (Ig) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | G_PTOC1_OpDlTm | Ground Fault protection setting | G_PTOC1_OpDlTm | Ground Fault (GF): Delay (tg) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | EF_PTOC1_Mod | Earth Fault protection setting | EF_PTOC1_Mod | Earth Fault (EF) Protection ON | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | EF_PTOC1_StrVal | Earth Fault protection setting | EF_PTOC1_StrVal | Earth Fault (EF): Pick-Up Value (I∆n) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | EF_PTOC1_OpDlTm | Earth Fault protection setting | EF_PTOC1_OpDlTm | Earth Fault (EF): Delay (t∆n) setting | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | LPHD1_PolesNum | Nb of poles | LPHD1_PolesNum | tetra (3P+N) or tri (3P) | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | LPHD1_VRtg | Rated Voltage | LPHD1_VRtg | Rated Voltage | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | LPHD1_ProtectionType | Protection Type | LPHD1_ProtectionType | Protection Type | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X |  | LPHD1_ApplicationType | Application Type | LPHD1_ApplicationType | Application : 1 = distribution, 2 = motor | Events Group | ProtSetChangeHMI, ProtSetChangeComm | 60 | 86400 | asap |  |  | Simple | None | No | No
ACB Breakers Masterpact MTZ - µLogic X
Acti9 SmartLink digital auxilaries TI24
Acti9 SmartLink digital auxilaries TI24 | Acti9 iOF+SD24 top connector Acti9 iOF+SD24 bottom connector Acti9 RCAiC60 Acti9 Reflex iC60 Acti9 OF24 ActI9 SD24
Acti9 SmartLink digital auxilaries TI24
Wireless environmental sensor HeatTag
Wireless environmental sensor HeatTag | HeatTag cable overheating sensor
Wireless environmental sensor HeatTag |  | CALH1_HeatAlmHigh | Cable Overheating | CALH1_HeatAlmHigh | cable overheating Alert notification | Unique | CALH1_HeatAlmHigh | 30 | na | asap |  |  | Simple | High | Yes | No
Wireless environmental sensor HeatTag |  | CALH1_HeatAlmMedium | Cable Overheating | CALH1_HeatAlmMedium | cable overheating Alert notification | Unique | CALH1_HeatAlmMedium | 30 | na | asap |  |  | Simple | High | Yes | No | severity to be confirmed.
Wireless environmental sensor HeatTag |  | CALH1_HeatAlmLow | Cable Overheating | CALH1_HeatAlmLow | cable overheating Alert notification | Unique | CALH1_HeatAlmLow | 30 | na | asap |  |  | Simple | High | Yes | No | severity to be confirmed.
Wireless environmental sensor HeatTag |  | CALH1_CommLoss | Communication | CALH1_CommLoss | Communication Loss | Unique | CALH1_CommLoss | 90 | na | asap |  |  | Simple | Low | Yes | No
TransferPact Active Automatic (Ruby/Ruby+)
TransferPact Active Automatic (Ruby/Ruby+)
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_Pos | Transfer Switch Status | ATS.AATS1_Pos | Transfer Switch Status | Unique | ATS.AATS1_Pos | 15 | 86400 | asap |  |  | Simple | High | Yes | No | FE Notification through ZAC & PaS (Interest tbc by FE Team) / Same comment for EEH
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_SrcN_DetSt | Normal Source State | ATS.AATS1_SrcN_DetSt | Normal Source State | Unique | ATS.AATS1_SrcN_DetSt | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_SrcA_DetSt | Alternate Source State | ATS.AATS1_SrcA_DetSt | Alternate Source State | Unique | ATS.AATS1_SrcA_DetSt | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S1.RvPPV_PTOV1_Str | S1 phase Sequence error | S1.RvPPV_PTOV1_Str | S1 phase Sequence error | Unique | S1.RvPPV_PTOV1_Str | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S1.Neutral1_WirePos | S1 neutral position wrong | S1.Neutral1_WirePos | S1 neutral position wrong | Unique | S1.Neutral1_WirePos | 15 | 86400 | asap |  | ATS.LPHD1_PolesCfg | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S1.UnbPPV_PTOV1_Str | S1 unbalance voltage status | S1.UnbPPV_PTOV1_Str | S1 unbalance voltage status | Unique | S1.UnbPPV_PTOV1_Str | 15 | 86400 | asap |  | S1.VUnbalLLW S1.UnbPPV_PTOV1_StrVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S1.Neutral1_WireLoss | S1 neutral loss alarm | S1.Neutral1_WireLoss | S1 neutral loss alarm | Unique | S1.Neutral1_WireLoss | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S1.PTOV1_Str | S1 over voltage state | S1.PTOV1_Str | S1 over voltage state | Unique | S1.PTOV1_Str | 15 | 86400 | asap |  | S1.VAB S1.VBC S1.VCA S1.VAN S1.VBN S1.VCN ATS.LPHD1_VRtg S1.PTOV1_StrValCoef S1.PTOV1_StrRsValCoef S1.PTOV1_StrVal S1.PTOV1_StrRsVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S1.PTUV1_Str | S1 under voltage state | S1.PTUV1_Str | S1 under voltage state | Unique | S1.PTUV1_Str | 15 | 86400 | asap |  | S1.VAB S1.VBC S1.VCA S1.VAN S1.VBN S1.VCN ATS.LPHD1_VRtg S1.PTUV1_StrValCoef S1.PTUV1_StrRsValCoef S1.PTUV1_StrVal S1.PTUV1_StrRsVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S1.PTOF1_Str | S1 over frequency state | S1.PTOF1_Str | S1 over frequency state | Unique | S1.PTOF1_Str | 15 | 86400 | asap |  | S1.Hz ATS.LPHD1_HzRtg S1.PTOF1_StrValCoef S1.PTOF1_StrRsValCoef S1.PTOF1_StrVal S1.PTOF1_StrRsVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S1.PTUF1_Str | S1 under frequency state | S1.PTUF1_Str | S1 under frequency state | Unique | S1.PTUF1_Str | 15 | 86400 | asap |  | S1.Hz ATS.LPHD1_HzRtg S1.PTUF1_StrValCoef S1.PTUF1_StrRsValCoef S1.PTUF1_StrVal S1.PTUF1_StrRsVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S2.RvPPV_PTOV1_Str | S2 phase Sequence error | S2.RvPPV_PTOV1_Str | S2 phase Sequence error | Unique | S2.RvPPV_PTOV1_Str | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S2.Neutral1_WirePos | S2 neutral position wrong | S2.Neutral1_WirePos | S2 neutral position wrong | Unique | S2.Neutral1_WirePos | 15 | 86400 | asap |  | ATS.LPHD1_PolesCfg | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S2.UnbPPV_PTOV1_Str | S2 unbalance voltage status | S2.UnbPPV_PTOV1_Str | S2 unbalance voltage status | Unique | S2.UnbPPV_PTOV1_Str | 15 | 86400 | asap |  | S2.VUnbalLLW S2.UnbPPV_PTOV1_StrVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S2.Neutral1_WireLoss | S2 neutral loss alarm | S2.Neutral1_WireLoss | S2 neutral loss alarm | Unique | S2.Neutral1_WireLoss | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S2.PTOV1_Str | S2 over voltage state | S2.PTOV1_Str | S2 over voltage state | Unique | S2.PTOV1_Str | 15 | 86400 | asap |  | S2.VAB S2.VBC S2.VCA S2.VAN S2.VBN S2.VCN ATS.LPHD1_VRtg S2.PTOV1_StrValCoef S2.PTOV1_StrRsValCoef S2.PTOV1_StrVal S2.PTOV1_StrRsVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S2.PTUV1_Str | S2 under voltage state | S2.PTUV1_Str | S2 under voltage state | Unique | S2.PTUV1_Str | 15 | 86400 | asap |  | S2.VAB S2.VBC S2.VCA S2.VAN S2.VBN S2.VCN ATS.LPHD1_VRtg S2.PTUV1_StrValCoef S2.PTUV1_StrRsValCoef S2.PTUV1_StrVal S2.PTUV1_StrRsVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S2.PTOF1_Str | S2 over frequency state | S2.PTOF1_Str | S2 over frequency state | Unique | S2.PTOF1_Str | 15 | 86400 | asap |  | S2.Hz ATS.LPHD1_HzRtg S2.PTOF1_StrValCoef S2.PTOF1_StrRsValCoef S2.PTOF1_StrVal S2.PTOF1_StrRsVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | S2.PTUF1_Str | S2 under frequency state | S2.PTUF1_Str | S2 under frequency state | Unique | S2.PTUF1_Str | 15 | 86400 | asap |  | S2.Hz ATS.LPHD1_HzRtg S2.PTUF1_StrValCoef S2.PTUF1_StrRsValCoef S2.PTUF1_StrVal S2.PTUF1_StrRsVal | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_LS_CtlSt | Load shedding status | ATS.AATS1_LS_CtlSt | Load shedding status | Unique | ATS.AATS1_LS_CtlSt | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_Generator_CtlSt | Genset control status | ATS.AATS1_Generator_CtlSt | Genset control status | Unique | ATS.AATS1_Generator_CtlSt | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.LPHD1_OpSt | Runtime mode | ATS.LPHD1_OpSt | Runtime mode | Unique | ATS.LPHD1_OpSt | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.PMSS1_OpReq | Genset start failure alarm | ATS.PMSS1_OpReq | Genset start failure alarm | Unique | ATS.PMSS1_OpReq | 60 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.Test1_OnloadRsl | Onload test failure alarm | ATS.Test1_OnloadRsl | Onload test failure alarm | Unique | ATS.Test1_OnloadRsl | 60 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.Test1_OffloadRsl | Offload test failure alarm | ATS.Test1_OffloadRsl | Offload test failure alarm | Unique | ATS.Test1_OffloadRsl | 60 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_PosErrCtx | Unexpected position alarm | ATS.AATS1_PosErrCtx | Unexpected position alarm | Unique | ATS.AATS1_PosErrCtx | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | LPHD1_ConfChgCnt | Configuration changed count | LPHD1_ConfChgCnt | Configuration changed count | Unique | LPHD1_ConfChgCnt | 60 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_TrfOff_St | Force to off status | ATS.AATS1_TrfOff_St | Force to off status | Unique | ATS.AATS1_TrfOff_St | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_TrfOff_St | Inhibit status | ATS.AATS1_TrfOff_St | Inhibit status | Unique | ATS.AATS1_TrfOff_St | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_TrfPrio_St | Voluntary control status | ATS.AATS1_TrfPrio_St | Voluntary control status | Unique | ATS.AATS1_TrfPrio_St | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  | ATS.AATS1_TrfFire_St | Fire status | ATS.AATS1_TrfFire_St | Fire status | Unique | ATS.AATS1_TrfFire_St | 15 | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  |  |  | 0 | 0 |  | 0 |  | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+) |  |  |  | 0 | 0 |  | 0 |  | 86400 | asap |  |  | Simple |  | No | No
TransferPact Active Automatic (Ruby/Ruby+)
TransferPact Active Automatic (Ruby/Ruby+)
TransferPact Active Automatic (Ruby/Ruby+)
TransferPact Active Automatic (Ruby/Ruby+)
MCB Breakers A9 Active (Quattro & Smart RCD)
MCB Breakers A9 Active (Quattro & Smart RCD)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_VLoss3PhsAlm | Vloss Status | CALH1_VLoss3PhsAlm | Voltage loss 3 phases status alarm | Unique | CALH1_VLoss3PhsAlm | 60 | na | asap |  |  | Simple | High | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | XCBR1_Pos | OF Status | XCBR1_Pos | OF Status | Unique | XCBR1_Pos | 60 | na | asap |  |  | Simple | Low | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_MaintPrMAlm | Threshold based alarm | CALH1_MaintPrMAlm | Trip Test not performed alarm | Unique | CALH1_MaintPrMAlm | 60 | na | asap |  |  | Simple | Low | Yes | No | Trip Test Not performed Event: period to configure in PaS
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_UVCoef080Alm | Threshold based alarm | CALH1_UVCoef080Alm | Under voltage alarm | Unique | CALH1_UVCoef080Alm | 60 | na | asap |  |  | Simple | High | Yes | No | Under Voltage Alarm with threshold at 80% of nominal voltage. Nominal voltage to be set in PaS. Alarm selectable in PaS (?)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_OVCoef120Alm | Threshold based alarm | CALH1_OVCoef120Alm | Over voltage alarm | Unique | CALH1_OVCoef120Alm | 60 | na | asap |  |  | Simple | High | Yes | No | Over Voltage Alarm with threshold at 120% of nominal voltage. Nominal voltage to be set in PaS. Alarm selectable in PaS (?)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_ILossAlm | Threshold based alarm | CALH1_ILossAlm | Zero current alarm | Unique | CALH1_ILossAlm | 60 | na | asap |  |  | Simple | High | Yes | No | Selectable in PaS (?)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_OCCoef045Alm | Threshold based alarm | CALH1_OCCoef045Alm | Over current 45% alarm | Unique | CALH1_OCCoef045Alm | 60 | na | asap |  |  | Simple | High | Yes | No | Selectable in PaS (?)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_OCCoef050Alm | Threshold based alarm | CALH1_OCCoef050Alm | Over current 50% alarm | Unique | CALH1_OCCoef050Alm | 60 | na | asap |  |  | Simple | High | Yes | No | Selectable in PaS (?)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_OCCoef080Alm | Threshold based alarm | CALH1_OCCoef080Alm | Over current 80% alarm | Unique | CALH1_OCCoef080Alm | 60 | na | asap |  |  | Simple | High | Yes | No | Selectable in PaS (?)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_IOverloadAlm | pre alarm | CALH1_IOverloadAlm | Over current pre alarm | Unique | CALH1_IOverloadAlm | 60 | na | asap |  |  | Simple | Low | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_OverVAlm | pre alarm | CALH1_OverVAlm | Over voltage pre alarm | Unique | CALH1_OverVAlm | 60 | na | asap |  |  | Simple | Low | Yes | No | Nominal voltage to be set in PaS. Alarm selectable in PaS (?)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | CALH1_AEFAlm | pre alarm | CALH1_AEFAlm | Earth leakage pre alarm | Unique | CALH1_AEFAlm | 60 | na | asap |  |  | Simple | Low | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | PTOV1_Op | Trip alarm | PTOV1_Op | Over voltage trip alarm | Unique | PTOV1_Op | 60 | na | asap |  |  | Simple | High | Yes | No | Nominal voltage to be set in PaS. Alarm selectable in PaS (?)
MCB Breakers A9 Active (Quattro & Smart RCD) |  | Pro_Test1_Op | Trip alarm | Pro_Test1_Op | Test push button trip alarm | Unique | Pro_Test1_Op | 60 | na | asap |  |  | Simple | High | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | LPHD1_IntErr | Trip alarm | LPHD1_IntErr | Internal cause trip alarm | Unique | LPHD1_IntErr | 60 | na | asap |  |  | Simple | High | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | XCBR1_TripChainOp | Trip alarm | XCBR1_TripChainOp | Tripping chain failure trip alarm | Unique | XCBR1_TripChainOp | 60 | na | asap |  |  | Simple | High | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | LT_PTOC1_Op | Trip alarm | LT_PTOC1_Op | Long Time (LT) trip alarm | Unique | LT_PTOC1_Op | 60 | na | asap |  |  | Simple | High | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | ST_PTOC1_Op | Trip alarm | ST_PTOC1_Op | Short Time (ST) trip alarm | Unique | ST_PTOC1_Op | 60 | na | asap |  |  | Simple | High | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD) |  | EF_PTOC1_Op | Trip alarm | EF_PTOC1_Op | Earth leakage (EF) trip alarm | Unique | EF_PTOC1_Op | 60 | na | asap |  |  | Simple | High | Yes | No
MCB Breakers A9 Active (Quattro & Smart RCD)
MCB Breakers A9 Active (Quattro)
MCB Breakers A9 Active (Quattro)
MCB Breakers A9 Active (Quattro) |  | SARC1_SerOp | Trip alarm | SARC1_SerOp | Arc fault serial protection trip alarm | Unique | SARC1_SerOp | 60 | na | asap |  |  | Simple | High | Yes | No
MCB Breakers A9 Active (Quattro) |  | SARC1_ParOp | Trip alarm | SARC1_ParOp | Arc fault parallel protection trip alarm | Unique | SARC1_ParOp | 60 | na | asap |  |  | Simple | High | Yes | No
Note on J6: based on the fact that 3 subsequent publications (1/8hours) are missing
Note on J30: based on the fact that 3 subsequent publications (1/8hours) are missing
Note on C130: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be confirmed (if y = consistent with predefined events Compact NSX & Compact NS - Masterpact NT-NW
Note on C132: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: tbc if similar as: LT_PTOC1_Op used for compact NSX (same question for the next lines)
Note on G150: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be confirm (same mechanism as for NSX with data = Maint_GLOG1_EntryEvtDT ?)
Note on H150: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: to be confirm (same mechanism as for NSX with data = Maint_GLOG1_EntryEvtDT ?)
Note on I183: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I184: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G185: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H185: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I185: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G187: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H187: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I187: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G188: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H188: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I188: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G189: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H189: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I189: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G190: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H190: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I190: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G192: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H192: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I192: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G193: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H193: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I193: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G194: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H194: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I194: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G195: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H195: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I195: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G196: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H196: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I196: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G198: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H198: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I198: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I199: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G201: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H201: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I201: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G202: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H202: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I202: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G203: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H203: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I203: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I204: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I205: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I206: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I207: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on C210: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G210: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H210: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I210: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on C211: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G211: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H211: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I211: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on G212: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on H212: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I212: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed
Note on I213: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be confirmed